## DGA
S. No. | DGA Analysis (IS 10593,9434) test value in ppm (Parts-per-million) | [14 empty] | Rogers Ratio Method | [5 empty] | IEC Ratio Method | [5 empty] | Dornenburg Ratio Method
| SR. NO. | Rating | Ratio(KV) | Make | Year of Manufacture | TGC Total Gas Content | H2 Hydrogen | O2 Oxygen | N2 Nitrogen | CO Carbomonoxide | CO2 Carbondioxide | CH4 Methane | C2H6 Ethane | C2H4 Ethylene | C2H2 Acetyline | C2H2/C2H4 | CH4/H2 | C2H4/C2H6 | FAULT TYPE |  |  | C2H2/C2H4 | CH4/H2 | C2H4/C2H6 | FAULT TYPE |  |  | CH4/H2 | C2H2/C2H4 | C2H2/CH4 | C2H6/C2H2 | FAULT TYPE
1 | HT-1869/13207 | 50 MVA | 66/0.433 KV | EMCO | 2010 | 8.4 | 1.176 | 15746.136 | 65474.976 | 153.636 | 1468.488 | 1.008 | 2 | 1 | 3 | 3 | 0.8571428571 | 0.5 | Arching | Arching,Low temprature thermal fault | Arching,Thermal Fault > 700 c | 3 | 0.8571428571 | 0.5 | Thermal Faults>700c | High Energy Discharge | thermal fault <300 | 0.8571428571 | 3 | 2.976190476 | 0.6 | Arching | Arching | Arching | Thermal Decomposition,corona
2 | HT-1869/13207 | 50 MVA | 66/0.433 KV | EMCO | 2010 | 8.6 | 954.17 | 15964.868 | 65313.904 | 44.806 | 568.546 | 118.594 | 27.09 | 816.57 | 1077.15 | 1.319115324 | 0.1242902208 | 30.14285714 | Arching | Arching,Low temprature thermal fault | Arching,Thermal Fault > 700 c | 1.319115324 | 0.1242902208 | 30.14285714 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.1242902208 | 1.319115324 | 9.0826686 | 0.0251497006 | Arching | Arching | Arching | Arching
3 | HT-1869/13207 | 50 MVA | 66/0.433 KV | EMCO | 2010 | 8.4 | 2.94 | 15616.86 | 65702.784 | 161.364 | 1648.248 | 7 | 9 | 11 | 9 | 0.8181818182 | 2.380952381 | 1.222222222 | Arching | Arching | Low Temprature thermal Fault,Thermal Fault<700c | 0.8181818182 | 2.380952381 | 1.222222222 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 2.380952381 | 0.8181818182 | 1.285714286 | 1 | Thermal Decomposition | Arching | Arching | Thermal Decomposition,corona
4 | B-22806(DIT-000055) | 10 MVA | 33/11 KV | THE GENERAL ELECTRICAL | 1982 | 8.2 | 9.348 | 15345.89 | 63123.928 | 196.226 | 2272.466 | 6 | 2.46 | 38.048 | 23 | 0.6044995795 | 0.6418485237 | 15.46666667 | Arching | Arching,Low temprature thermal fault | Arching,Thermal Fault > 700 c | 0.6044995795 | 0.6418485237 | 15.46666667 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.6418485237 | 0.6044995795 | 3.833333333 | 0.1069565217 | Arching | Thermal Decomposition, | Arching | Arching
5 | 1000060003(DIT-000026) | 10 MVA | 33/11 KV | PME | 2005 | 7.8 | 4.758 | 14397.006 | 60962.226 | 179.712 | 1573.494 | 2.184 | 6.162 | 8.658 | 12 | 1.386001386 | 0.4590163934 | 1.405063291 | Arching | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 1.386001386 | 0.4590163934 | 1.405063291 | Discharge of Low Energy, | High Energy Discharge | Thermal Fault >700 c | 0.4590163934 | 1.386001386 | 5.494505495 | 0.5135 | Arching | Arching | Arching | Thermal Decomposition,corona
6 | 172580(DIT-000090) | 10 MVA | 33/11 KV | RAJASTAN | 2006 | 8.2 | 5.904 | 15182.956 | 63176.162 | 223.532 | 2445.486 | 13.038 | 57.236 | 18.204 | 34 | 1.86772138 | 2.208333333 | 0.3180515759 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 1.86772138 | 2.208333333 | 0.3180515759 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300 | 2.208333333 | 1.86772138 | 2.607761927 | 1.683411765 | Thermal Decomposition | Arching | Arching | Thermal Decomposition,corona
7 | 10000000021 T-2204 | 10 MVA | 33/11 KV | PME | 2003 | 8.4 | 7.476 | 15497.244 | 65034.312 | 195.048 | 2150.904 | 13.02 | 111.3 | 27.3 | 43 | 1.575091575 | 1.741573034 | 0.2452830189 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 1.575091575 | 1.741573034 | 0.2452830189 | Discharge of Low Energy, | thermal fault<300 | thermal fault <300 | 1.741573034 | 1.575091575 | 3.302611367 | 2.588372093 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
8 | 172578 | 10 MVA | 33/11 KV | RAJASTAN | 2006 | 8.6 | 5.332 | 15666.792 | 66793.018 | 190.662 | 2283.3 | 2.15 | 13.33 | 5.59 | 10 | 1.788908766 | 0.4032258065 | 0.4193548387 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1.788908766 | 0.4032258065 | 0.4193548387 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300 | 0.4032258065 | 1.788908766 | 4.651162791 | 1.333 | Arching | Arching | Arching | Thermal Decomposition,corona
9 | TTL/UP25235 T-1960 | 10 MVA | 33/11 | TESLA TRANSFORMER | 2002 | 7.8 | 7.488 | 14384.994 | 59960.238 | 269.334 | 2765.334 | 18.954 | 7.722 | 31.122 | 25 | 0.803290277 | 2.53125 | 4.03030303 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Arching,Thermal Fault > 700 c | 0.803290277 | 2.53125 | 4.03030303 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 2.53125 | 0.803290277 | 1.3189828 | 0.30888 | Thermal Decomposition, | Arching | Arching | Arching
10 | 69546 | 10 MVA | 33/11 KV | MARSONS | 2012 | 8.1 | 5.589 | 15002.739 | 61258.113 | 353.808 | 3861.837 | 7.371 | 6 | 4 | 8 | 2 | 1.31884058 | 0.6666666667 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 2 | 1.31884058 | 0.6666666667 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300 | 1.31884058 | 2 | 1.085334419 | 0.75 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
11 | 69543 | 10 MVA | 33/11 KV | MARSONS | 2011 | 8.5 | 1.615 | 15602.43 | 65923.28 | 211.905 | 2347.105 | 5.525 | 5 | 5 | 4 | 0.8 | 3.421052632 | 1 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 0.8 | 3.421052632 | 1 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | High energhy Discharge | 3.421052632 | 0.8 | 0.7239819005 | 1.25 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
12 | 69542 | 10 MVA | 33/11 KV | MARSONS | 2011 | 8.4 | 8.064 | 15280.356 | 64058.484 | 396.564 | 3724.728 | 11.34 | 10 | 10 | 8 | 0.8 | 1.40625 | 1 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 0.8 | 1.40625 | 1 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | High energhy Discharge | 1.40625 | 0.8 | 0.7054673721 | 1.25 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
13 | 69545 | 10 MVA | 33/11 KV | MARSONS | 2012 | 8.2 | 3.69 | 15127.688 | 64168.772 | 174.086 | 2084.85 | 5.33 | 4.018 | 8.856 | 8 | 0.9033423668 | 1.444444444 | 2.204081633 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 0.9033423668 | 1.444444444 | 2.204081633 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.444444444 | 0.9033423668 | 1.500938086 | 0.50225 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
14 | ATL-10187070001 | 10 MVA | 33/11 KV | ACCURATE | 2008 | 8.4 | 5.124 | 15196.272 | 65697.072 | 185.304 | 2039.604 | 2.94 | 2.1 | 5.796 | 5 | 0.8626639061 | 0.5737704918 | 2.76 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.8626639061 | 0.5737704918 | 2.76 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.5737704918 | 0.8626639061 | 1.700680272 | 0.42 | Arching | Arching | Arching | Thermal Decomposition,corona
15 | 2165 | 10 MVA | 33/11 KV | PARTICULAR | 2013 | 8.5 | 8.415 | 15522.955 | 65567.385 | 233.58 | 2540.48 | 7.225 | 9 | 8 | 8 | 1 | 0.8585858586 | 0.8888888889 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1 | 0.8585858586 | 0.8888888889 | High Energy Discharge | High Energy Discharge | High energhy Discharge | 0.8585858586 | 1 | 1.107266436 | 1.125 | Arching | Arching | Arching | Thermal Decomposition,corona
16 | 95589 | 10 MVA | 33/11 KV | MARSONS | 2015 | 8 | 9.52 | 14900.96 | 60161.52 | 387.84 | 3842.96 | 18.32 | 4.08 | 11.84 | 18 | 1.52027027 | 1.924369748 | 2.901960784 | Arching | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 1.52027027 | 1.924369748 | 2.901960784 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.924369748 | 1.52027027 | 0.9825327511 | 0.2266666667 | Thermal Decomposition, | Arching | Arching | Arching
17 | 62444 | 10 MVA | 33/11 KV | MARSONS | 2010 | 8.5 | 12.58 | 16844.025 | 60794.975 | 603.33 | 5941.755 | 21.675 | 16.065 | 114.92 | 100 | 0.8701705534 | 1.722972973 | 7.153439153 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Arching,Thermal Fault > 700 c | 0.8701705534 | 1.722972973 | 7.153439153 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.722972973 | 0.8701705534 | 4.61361015 | 0.16065 | Thermal Decomposition, | Arching | Arching | Arching
18 | T-2228 | 10 MVA | 33/11 KV | KATSONS | 2013 | 8.2 | 1.558 | 14378.454 | 65308.49 | 134.726 | 1422.618 | 7.298 | 11 | 9 | 6 | 0.6666666667 | 4.684210526 | 0.8181818182 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 0.6666666667 | 4.684210526 | 0.8181818182 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | High energhy Discharge | 4.684210526 | 0.6666666667 | 0.8221430529 | 1.833333333 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
19 | 103757 | 10 MVA | 33/11 KV | MARSONS | 2019 | 8.2 | 8.036 | 14956.554 | 64368.77 | 168.592 | 1772.102 | 4.182 | 15 | 8 | 8 | 1 | 0.5204081633 | 0.5333333333 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1 | 0.5204081633 | 0.5333333333 | High Energy Discharge | High Energy Discharge | High energhy Discharge | 0.5204081633 | 1 | 1.912960306 | 1.875 | Arching | Arching | Arching | Thermal Decomposition,corona
20 | 102146 | 10 MVA | 33/11 KV | MARSONS | 2017 | 8.5 | 6.63 | 15460.735 | 65784.22 | 249.305 | 2536.06 | 7.225 | 9 | 9 | 3 | 0.3333333333 | 1.08974359 | 1 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 0.3333333333 | 1.08974359 | 1 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | High energhy Discharge | 1.08974359 | 0.3333333333 | 0.4152249135 | 3 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
21 | 96591 | 10 MVA | 33/11 KV | MARSONS | 2015 | 7.8 | 9.594 | 14803.152 | 59331.48 | 290.472 | 2714.79 | 17.784 | 8 | 7.722 | 9 | 1.165501166 | 1.853658537 | 0.96525 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 1.165501166 | 1.853658537 | 0.96525 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | High energhy Discharge | 1.853658537 | 1.165501166 | 0.5060728745 | 0.8888888889 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
22 | 109394 | 10 MVA | 33/11 KV | MARSONS | 2020 | 8.1 | 2.106 | 14994.639 | 64523.304 | 94.608 | 898.047 | 6 | 7 | 8 | 10 | 1.25 | 2.849002849 | 1.142857143 | Arching | Low temperature thermal | Low Temprature thermal Fault,Thermal Fault<700c | 1.25 | 2.849002849 | 1.142857143 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 2.849002849 | 1.25 | 1.666666667 | 0.7 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
23 | 110120 | 10 MVA | 33/11 KV | MARSONS | 2020 | 8.4 | 3 | 15372.084 | 67096.092 | 49.392 | 558.768 | 7 | 6 | 6 | 34 | 5.666666667 | 2.333333333 | 1 | Arching | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 5.666666667 | 2.333333333 | 1 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300 c | 2.333333333 | 5.666666667 | 4.857142857 | 0.1764705882 | Thermal Decomposition, | Arching | Arching | Arching
24 | 109392 | 10 MVA | 33/11 KV | MARSONS | 2020 | 8.4 | 3.948 | 15735.972 | 66306.156 | 72.66 | 751.884 | 9 | 11 | 8 | 17 | 2.125 | 2.279635258 | 0.7272727273 | Arching | Low temperature thermal | Partial discharge, Normal | 2.125 | 2.279635258 | 0.7272727273 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300 c | 2.279635258 | 2.125 | 1.888888889 | 0.6470588235 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
25 | 109395 | 10 MVA | 33/11 KV | MARSONS | 2020 | 8.2 | 6 | 14969.182 | 65210.254 | 76.67 | 836.892 | 5 | 12 | 6 | 17 | 2.833333333 | 0.8333333333 | 0.5 | Arching | Arching | Partial discharge, Normal | 2.833333333 | 0.8333333333 | 0.5 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300 c | 0.8333333333 | 2.833333333 | 3.4 | 0.7058823529 | Arching | Arching | Arching | Thermal Decomposition,corona
26 | 107358 | 10 MVA | 33/11 KV | MARSONS | 2019 | 8 | 7 | 14494.72 | 62801.68 | 158.08 | 1702.24 | 3 | 9 | 8 | 34 | 4.25 | 0.4285714286 | 0.8888888889 | Arching | Arching | Partial discharge, Normal | 4.25 | 0.4285714286 | 0.8888888889 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300 c | 0.4285714286 | 4.25 | 11.33333333 | 0.2647058824 | Arching | Arching | Arching | Arching
27 | 109393 | 10 MVA | 33/11 KV | MARSONS | 2020 | 8.3 | 9 | 15162.108 | 66073.644 | 79.763 | 842.035 | 9 | 11 | 7 | 9 | 1.285714286 | 1 | 0.6363636364 | Arching | Arching | Partial discharge, Normal | 1.285714286 | 1 | 0.6363636364 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300 c | 1 | 1.285714286 | 1 | 1.222222222 | Arching | Arching | Arching | Thermal Decomposition,corona
28 | 102145 | 10 MVA | 33/11 KV | MARSONS | 2017 | 8.5 | 3.74 | 15646.29 | 67067.635 | 110.415 | 933.64 | 5.865 | 14 | 5 | 12 | 2.4 | 1.568181818 | 0.3571428571 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 2.4 | 1.568181818 | 0.3571428571 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300 c | 1.568181818 | 2.4 | 2.046035806 | 1.166666667 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
29 | 103754 | 10 MVA | 33/11 KV | MARSONS | 2018 | 8.3 | 12.948 | 15300.469 | 64967.752 | 161.601 | 1625.887 | 4.067 | 11 | 7 | 45 | 6.428571429 | 0.3141025641 | 0.6363636364 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 6.428571429 | 0.3141025641 | 0.6363636364 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300 c | 0.3141025641 | 6.428571429 | 11.06466683 | 0.2444444444 | Arching | Arching | Arching | Arching
30 | 103756 | 10 MVA | 33/11 KV | MARSONS | 2019 | 8.5 | 16.83 | 16032.615 | 66596.565 | 155.975 | 1646.195 | 9 | 14 | 9 | 37 | 4.111111111 | 0.5347593583 | 0.6428571429 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 4.111111111 | 0.5347593583 | 0.6428571429 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300 c | 0.5347593583 | 4.111111111 | 4.111111111 | 0.3783783784 | Arching | Arching | Arching | Arching
31 | 102147 | 10 MVA | 33/11 KV | MARSONS | 2017 | 8.4 | 8.316 | 15461.796 | 64806.084 | 249.564 | 2456.58 | 8.232 | 6.468 | 5 | 38 | 7.6 | 0.9898989899 | 0.7730364873 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 7.6 | 0.9898989899 | 0.7730364873 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300 c | 0.9898989899 | 7.6 | 4.616132167 | 0.1702105263 | Arching | Arching | Arching | Arching
32 | 109620(TIT005184) | 10 MVA | 33/11 KV | MARSONS | 2021 | 8.4 | 3 | 15346.716 | 66991.848 | 48.468 | 544.572 | 6 | 13 | 9 | 9 | 1 | 2 | 0.6923076923 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 1 | 2 | 0.6923076923 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300 c | 2 | 1 | 1.5 | 1.444444444 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
33 | 109618(TIT005718) | 10 MVA | 33/11 KV | MARSONS | 2015 | 8.3 | 4.814 | 15187.174 | 62781.615 | 375.492 | 3515.548 | 10.126 | 8.217 | 5 | 2 | 0.4 | 2.103448276 | 0.6084945844 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 0.4 | 2.103448276 | 0.6084945844 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300 c | 2.103448276 | 0.4 | 0.1975113569 | 4.1085 | Thermal Decomposition, | Thermal Decomposition, | Thermal Decomposition,corona | Thermal Decomposition,corona
34 | 172827(DIT000018) | 10 MVA | 33/11 KV | MARSONS | 2021 | 8.1 | 7 | 14919.633 | 64300.473 | 53.784 | 547.965 | 9 | 9 | 9 | 56 | 6.222222222 | 1.285714286 | 1 | Arching | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 6.222222222 | 1.285714286 | 1 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300 c | 1.285714286 | 6.222222222 | 6.222222222 | 0.1607142857 | Thermal Decomposition, | Arching | Arching | Arching
35 | 172827 | 10 MVA | 33/11 KV | RAJASTAN | 2008 | 8.5 | 8.415 | 15806.6 | 66676.55 | 160.395 | 1769.955 | 5.355 | 7 | 5 | 78 | 15.6 | 0.6363636364 | 0.7142857143 | Arching | Low temperature thermal | Partial discharge, Normal | 15.6 | 0.6363636364 | 0.7142857143 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300 c | 0.6363636364 | 15.6 | 14.56582633 | 0.08974358974 | Arching | Arching | Arching | Arching
36 | 172583 | 10 MVA | 33/11 KV | RAJASTAN | 2006 | 8.2 | 5.084 | 14945.648 | 64417.806 | 166.87 | 1974.478 | 5.166 | 7.298 | 3.69 | 8 | 2.16802168 | 1.016129032 | 0.5056179775 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 2.16802168 | 1.016129032 | 0.5056179775 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300 c | 1.016129032 | 2.16802168 | 1.548586914 | 0.91225 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
37 | 109617(TIT0057147) | 10 MVA | 33/11 KV | MARSONS | 2021 | 8.5 | 1.275 | 15541.74 | 67965.405 | 63.665 | 654.245 | 9 | 11 | 5 | 9 | 1.8 | 7.058823529 | 0.4545454545 | Arching | Low temperature thermal | Partial discharge, Normal | 1.8 | 7.058823529 | 0.4545454545 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300 c | 7.058823529 | 1.8 | 1 | 1.222222222 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
38 | 172521(DIT000064) | 10 MVA | 33/11 | RAJSTHAN TRANSFORMER | 2006 | 8.3 | 7.968 | 15116.126 | 64924.011 | 163.925 | 1848.908 | 7.968 | 2.988 | 7 | 5 | 0.7142857143 | 1 | 2.34270415 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.7142857143 | 1 | 2.34270415 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 1 | 0.7142857143 | 0.6275100402 | 0.5976 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
39 | DIT000072 | 10 MVA | 33/11 KV | -- | -- | 8.2 | 1.558 | 15084.392 | 64294.478 | 141.696 | 1555.048 | 6 | 8 | 9 | 34 | 3.777777778 | 3.851091142 | 1.125 | Arching | Low temperature thermal | Low Temprature thermal Fault,Thermal Fault<700c | 3.777777778 | 3.851091142 | 1.125 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 3.851091142 | 3.777777778 | 5.666666667 | 0.2352941176 | Thermal Decomposition, | Arching | Arching | Arching
40 | 109396 | 10 MVA | 33/11 KV | MARSONS | 2020 | 8.2 | 4.018 | 15194.108 | 64724.158 | 80.934 | 976.784 | 5 | 9 | 5 | 56 | 11.2 | 1.244400199 | 0.5555555556 | Arching | Low temperature thermal | Partial discharge, Normal | 11.2 | 1.244400199 | 0.5555555556 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300 | 1.244400199 | 11.2 | 11.2 | 0.1607142857 | Thermal Decomposition, | Arching | Arching | Arching
41 | 103753 | 10 MVA | 33/11 KV | MARSONS | 2018 | 8.5 | 15.98 | 15494.14 | 66367.065 | 238.17 | 2236.095 | 6.205 | 5 | 9 | 78 | 8.666666667 | 0.3882978723 | 1.8 | Arching | Low temperature thermal | Low Temprature thermal Fault,Thermal Fault<700c | 8.666666667 | 0.3882978723 | 1.8 | Discharge of Low Energy, | High Energy Discharge | Thermal Fault >700 c | 0.3882978723 | 8.666666667 | 12.57050766 | 0.0641025641 | Arching | Arching | Arching | Arching
42 | 96588 | 10 MVA | 33/11 KV | MARSONS | 2015 | 8.1 | 2.835 | 15295.473 | 60813.909 | 406.863 | 3858.273 | 11.178 | 7.371 | 5 | 45 | 9 | 3.942857143 | 0.6783340117 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 9 | 3.942857143 | 0.6783340117 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300 | 3.942857143 | 9 | 4.025764895 | 0.1638 | Thermal Decomposition, | Arching | Arching | Arching
43 | 109391 | 10 MVA | 33/11 KV | MARSONS | 2020 | 8.4 | 7.476 | 15429.288 | 66204.012 | 115.164 | 1180.788 | 8 | 11 | 9 | 23 | 2.555555556 | 1.070090958 | 0.8181818182 | Arching | Low temperature thermal | Partial discharge, Normal | 2.555555556 | 1.070090958 | 0.8181818182 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <301 | 1.070090958 | 2.555555556 | 2.875 | 0.4782608696 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
44 | 96587 | 10 MVA | 33/11 KV | MARSONS | 2015 | 8.5 | 4.59 | 15529.16 | 65268.78 | 246.585 | 2827.185 | 7.565 | 15 | 5 | 56 | 11.2 | 1.648148148 | 0.3333333333 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 11.2 | 1.648148148 | 0.3333333333 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <302 | 1.648148148 | 11.2 | 7.402511566 | 0.2678571429 | Thermal Decomposition, | Arching | Arching | Arching
45 | A-0081910710007 | 10 MVA | 33/11 KV | AE | 2001 | 8.2 | 6.97 | 14893.578 | 63449.714 | 228.452 | 2317.484 | 10.496 | 7.872 | 3.69 | 4 | 1.08401084 | 1.505882353 | 0.46875 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 1.08401084 | 1.505882353 | 0.46875 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <303 | 1.505882353 | 1.08401084 | 0.381097561 | 1.968 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
46 | 10000000008 | 10 MVA | 33/11 KV | PME | 2003 | 8.6 | 1.892 | 16321.51 | 66716.736 | 142.33 | 1659.628 | 15.91 | 4.644 | 42.57 | 2 | 0.04698144233 | 8.409090909 | 9.166666667 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Arching,Thermal Fault > 700 c | 0.04698144233 | 8.409090909 | 9.166666667 | Thermal Fault> 300c and<700 c | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 8.409090909 | 0.04698144233 | 0.1257071025 | 2.322 | Thermal Decomposition, | Thermal Decomposition, | Thermal Decomposition,corona | Thermal Decomposition,corona
47 | 172579 | 10 MVA | 33/11 KV | RAJASTAN | 2006 | 8.3 | 6.059 | 15106.581 | 65421.928 | 139.523 | 1423.118 | 5.146 | 5.893 | 8 | 4 | 0.5 | 0.8493150685 | 1.357542847 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.5 | 0.8493150685 | 1.357542847 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.8493150685 | 0.5 | 0.7773027594 | 1.47325 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
48 | 100000000023(DIT000069) | 10 MVA | 33/11 KV | PME | 2003 | 8.3 | 1.66 | 14576.709 | 65447.409 | 182.766 | 2046.033 | 7.968 | 11 | 6.225 | 1 | 0.1606425703 | 4.8 | 0.5659090909 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 0.1606425703 | 4.8 | 0.5659090909 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300 | 4.8 | 0.1606425703 | 0.125502008 | 11 | Thermal Decomposition, | Thermal Decomposition, | Thermal Decomposition,corona | Thermal Decomposition,corona
49 | 172582 | 10 MVA | 33/11 KV | RAJSTHAN TRANSFORMER | 2006 | 8.2 | 5.658 | 14967.952 | 64167.952 | 164.082 | 1747.83 | 3.198 | 14 | 5.658 | 5 | 0.8837044892 | 0.5652173913 | 0.4041428571 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Partial discharge, Normal | 0.8837044892 | 0.5652173913 | 0.4041428571 | High Energy Discharge | High Energy Discharge | thermal fault <300 | 0.5652173913 | 0.8837044892 | 1.563477173 | 2.8 | Arching | Arching | Arching | Thermal Decomposition,corona
50 | 172527 | 10 MVA | 33/11 KV | RAJASTAN | 2006 | 8.2 | 8.036 | 15103.498 | 64099.81 | 178.76 | 1813.43 | 2.378 | 5 | 7.626 | 2 | 0.2622606871 | 0.2959183673 | 1.5252 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.2622606871 | 0.2959183673 | 1.5252 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.2959183673 | 0.2622606871 | 0.8410428932 | 2.5 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
51 | 103755 | 10 MVA | 33/11 KV | MARSONS | 2018 | 8.6 | 7.568 | 15732.324 | 67972.766 | 131.236 | 1377.548 | 9 | 7 | 8 | 6 | 0.75 | 1.189217759 | 1.142857143 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.75 | 1.189217759 | 1.142857143 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.189217759 | 0.75 | 0.6666666667 | 1.166666667 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
52 | 69544 | 10 MVA | 33/11 KV | MARSONS | 2012 | 8.3 | 7.968 | 15116.707 | 63337.881 | 276.888 | 3531.899 | 3.735 | 9 | 9 | 1 | 0.1111111111 | 0.46875 | 1 | Partial discharge,Low Temprature thermal fault, | Low temperature thermal | Low Temprature thermal Fault,Thermal Fault<700c | 0.1111111111 | 0.46875 | 1 | High Energy Discharge | High Energy Discharge | thermal fault <300 | 0.46875 | 0.1111111111 | 0.2677376171 | 9 | Arching | Thermal Decomposition, | Thermal Decomposition,corona | Thermal Decomposition,corona
53 | 109623(TIT005814) | 10 MVA | 33/11 KV | MARSONS | 2021 | 8.2 | 1.886 | 15013.462 | 65514.474 | 70.11 | 828.692 | 6 | 8 | 5 | 8 | 1.6 | 3.181336161 | 0.625 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1.6 | 3.181336161 | 0.625 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300 | 3.181336161 | 1.6 | 1.333333333 | 1 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
54 | 822804(DIT000094) | 10 MVA | 33/11 KV | GEC | 1982 | 8.6 | 11.008 | 15990.496 | 66990.302 | 189.802 | 2186.3522 | 7.396 | 7 | 6 | 5 | 0.8333333333 | 0.671875 | 0.8571428571 | Partial discharge,Low Temprature thermal fault, | Low temperature thermal | Partial discharge, Normal | 0.8333333333 | 0.671875 | 0.8571428571 | High Energy Discharge | High Energy Discharge | thermal fault <300 | 0.671875 | 0.8333333333 | 0.6760411033 | 1.4 | Arching | Arching | Arching | Thermal Decomposition,corona
55 | I100133/002 | 40 MVA | 132/11 KV | SIEMENS | 2014 | 8.2 | 7.626 | 15902.424 | 63598.216 | 115.21 | 1150.214 | 5.166 | 6 | 8 | 8 | 1 | 0.6774193548 | 1.333333333 | Arching | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 1 | 0.6774193548 | 1.333333333 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.6774193548 | 1 | 1.548586914 | 0.75 | Arching | Arching | Arching | Thermal Decomposition,corona
56 | I100133/001 | 40 MVA | 132/11 KV | SIEMENS | 2014 | 8 | 16.8 | 14509.28 | 63676.56 | 93.68 | 1194.4 | 6.48 | 12 | 9 | 3 | 0.3333333333 | 0.3857142857 | 0.75 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Partial discharge, Normal | 0.3333333333 | 0.3857142857 | 0.75 | High Energy Discharge | High Energy Discharge | thermal fault <300 | 0.3857142857 | 0.3333333333 | 0.462962963 | 4 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
57 | 2800046137 | 15 MVA | 132/11 KV | NGEF | 1988 | 8.5 | 68.765 | 16154.505 | 66137.99 | 136.935 | 1543.43 | 36.72 | 5.525 | 34 | 9 | 0.2647058824 | 0.5339925834 | 6.153846154 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Arching,Thermal Fault > 700 c | 0.2647058824 | 0.5339925834 | 6.153846154 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.5339925834 | 0.2647058824 | 0.2450980392 | 0.6138888889 | Arching | Thermal Decomposition, | Thermal Decomposition,corona | Thermal Decomposition,corona
58 | 2800046135 | 15 MVA | 132/11 KV | NGEF | 1988 | 8.5 | 11.305 | 15833.8 | 67642.235 | 75.48 | 873.29 | 5.865 | 9 | 3.825 | 6 | 1.568627451 | 0.5187969925 | 0.425 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1.568627451 | 0.5187969925 | 0.425 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300 | 0.5187969925 | 1.568627451 | 1.023017903 | 1.5 | Arching | Arching | Arching | Thermal Decomposition,corona
59 | 2800046136 | 15 MVA | 132/11 KV | NGEF | 1988 | 8.2 | 6.97 | 14974.512 | 64423.464 | 177.202 | 1816.218 | 8 | 9 | 6 | 7 | 1.166666667 | 1.147776184 | 0.6666666667 | Arching | Low temperature thermal | Partial discharge, Normal | 1.166666667 | 1.147776184 | 0.6666666667 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300 | 1.147776184 | 1.166666667 | 0.875 | 1.285714286 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
60 | 2800057667 | 28 MVA | 11/0.259 KV | NGEF | 1998 | 8.4 | 15.96 | 15142.26 | 64792.392 | 261.072 | 2690.016 | 6.048 | 9.66 | 5.796 | 5 | 0.8626639061 | 0.3789473684 | 0.6 | Partial discharge,Low Temprature thermal fault, | Low temperature thermal | Partial discharge, Normal | 0.8626639061 | 0.3789473684 | 0.6 | High Energy Discharge | High Energy Discharge | thermal fault <300 | 0.3789473684 | 0.8626639061 | 0.8267195767 | 1.932 | Arching | Arching | Arching | Thermal Decomposition,corona
61 | HT-1597/12313 | 28 MVA | 11/0.259 KV | EMCO | 2004 | 8.2 | 5.904 | 15859.292 | 63578.454 | 191.798 | 1826.714 | 4.346 | 2.788 | 9 | 13 | 1.444444444 | 0.7361111111 | 3.228120516 | Arching | Arching,Low temprature thermal fault | Arching,Thermal Fault > 700 c | 1.444444444 | 0.7361111111 | 3.228120516 | Discharge of Low Energy, | High Energy Discharge | Thermal Fault >700 c | 0.7361111111 | 1.444444444 | 2.991256328 | 0.2144615385 | Arching | Arching | Arching | Arching
62 | 280004-9527 | 15 MVA | 11/125 | NGEF | 1989 | 8.4 | 1.596 | 15757.308 | 65320.92 | 145.992 | 1763.328 | 5 | 9 | 8 | 14 | 1.75 | 3.13283208 | 0.8888888889 | Arching | Low temperature thermal | Partial discharge, Normal | 1.75 | 3.13283208 | 0.8888888889 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300 | 3.13283208 | 1.75 | 2.8 | 0.6428571429 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
63 | 2009726 | 80 MVA | 132/11.5 /6.9KV | BHEL | 1996 | 8.5 | 3.57 | 15349.64 | 66573.105 | 208.165 | 2072.555 | 9.18 | 2.635 | 7 | 8 | 1.142857143 | 2.571428571 | 2.65654649 | Arching | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 1.142857143 | 2.571428571 | 2.65654649 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 2.571428571 | 1.142857143 | 0.871459695 | 0.329375 | Thermal Decomposition, | Arching | Arching | Arching
64 | T/16881/C-10047 | 80 MVA | 132/11.5 /6.9KV | AREVA | 2011 | 8.5 | 14.365 | 15771.665 | 66289.375 | 170.34 | 2155.43 | 4.165 | 6 | 6 | 10 | 1.666666667 | 0.2899408284 | 1 | Arching | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 1.666666667 | 0.2899408284 | 1 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300 | 0.2899408284 | 1.666666667 | 2.400960384 | 0.6 | Arching | Arching | Arching | Thermal Decomposition,corona
65 | 280049973 | 15 MVA | 132/11.5 KV | NGEF | 1989 | 8.8 | 6.952 | 16446.32 | 68836.152 | 133.408 | 1649.824 | 8.008 | 8 | 8 | 6 | 0.75 | 1.151898734 | 1 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 0.75 | 1.151898734 | 1 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300 | 1.151898734 | 0.75 | 0.7492507493 | 1.333333333 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
66 | 120410 | 50 MVA | 132/11.5 KV | TELK | 1999 | 8.5 | 1.785 | 16681.335 | 64787.34 | 262.99 | 2541.585 | 6.205 | 9 | 1.955 | 8 | 4.092071611 | 3.476190476 | 0.2172222222 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 4.092071611 | 3.476190476 | 0.2172222222 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300 | 3.476190476 | 4.092071611 | 1.289282836 | 1.125 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
67 | T-8667/1 | 80 MVA | 132/11.5 KV | CG | 1999 | 8.2 | 5.166 | 16339.32 | 63727.448 | 93.152 | 1151.772 | 5.166 | 4 | 9 | 4 | 0.4444444444 | 1 | 2.25 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.4444444444 | 1 | 2.25 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 1 | 0.4444444444 | 0.7742934572 | 1 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
68 | 6003936 | 80 MVA | 132/11.5 KV | BHEL | 1975 | 8.5 | 1.785 | 16039.075 | 66231.915 | 129.795 | 1493.28 | 5.865 | 7.565 | 7 | 12 | 1.714285714 | 3.285714286 | 0.9253139458 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 1.714285714 | 3.285714286 | 0.9253139458 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300 | 3.285714286 | 1.714285714 | 2.046035806 | 0.6304166667 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
69 | 2012614 | 80 MVA | 132/11.5 KV | BHEL | 1999 | 8.6 | 9.374 | 15729.658 | 67789.242 | 116.444 | 1257.75 | 17.114 | 8 | 26.23 | 14 | 0.5337399924 | 1.825688073 | 3.27875 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Arching,Thermal Fault > 700 c | 0.5337399924 | 1.825688073 | 3.27875 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.825688073 | 0.5337399924 | 0.8180437069 | 0.5714285714 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
70 | TR-6650 B-30051 | 50 MVA | 132/11.5 KV | AREVA | 2006 | 8.2 | 12.71 | 14969.51 | 65471.178 | 95.612 | 940.458 | 10 | 11 | 8 | 6 | 0.75 | 0.7867820614 | 0.7272727273 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Partial discharge, Normal | 0.75 | 0.7867820614 | 0.7272727273 | High Energy Discharge | High Energy Discharge | thermal fault <300 | 0.7867820614 | 0.75 | 0.6 | 1.833333333 | Arching | FALSE | Arching | Thermal Decomposition,corona
71 | 2010654 | 50 MVA | 132/11.5 KV | BHEL | 1997 | 8.8 | 1.848 | 16360.608 | 68880.856 | 139.744 | 1453.584 | 5.544 | 10 | 3.784 | 8 | 2.114164905 | 3 | 0.3784 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 2.114164905 | 3 | 0.3784 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300 | 3 | 2.114164905 | 1.443001443 | 1.25 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
72 | 2010655 | 50 MVA | 132/11.5 KV | BHEL | 1997 | 8.2 | 7.626 | 15475.942 | 64339.168 | 145.632 | 1579.894 | 7.872 | 3.034 | 9 | 5 | 0.5555555556 | 1.032258065 | 2.966381015 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 0.5555555556 | 1.032258065 | 2.966381015 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.032258065 | 0.5555555556 | 0.6351626016 | 0.6068 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
73 | 2010653 | 16 MVA | 11.5/6.9 KV | BHEL | 1997 | 8.7 | 6.003 | 16578.459 | 68655.963 | 99.006 | 1010.592 | 6.612 | 7 | 2.523 | 7 | 2.774474832 | 1.101449275 | 0.3604285714 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 2.774474832 | 1.101449275 | 0.3604285714 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300 | 1.101449275 | 2.774474832 | 1.058681186 | 1 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
74 | 2010652 | 16 MVA | 11.5/6.9 KV | BHEL | 1997 | 8 | 4.72 | 15233.76 | 62455.04 | 115.92 | 1075.04 | 5.44 | 8 | 5 | 8 | 1.6 | 1.152542373 | 0.625 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 1.6 | 1.152542373 | 0.625 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300 | 1.152542373 | 1.6 | 1.470588235 | 1 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
75 | 5092/1 | 50 MVA | 132/11.5 KV | BBL | 2009 | 8.5 | 15.045 | 15660.655 | 65578.18 | 194.735 | 2535.72 | 10.88 | 9 | 8 | 12 | 1.5 | 0.7231638418 | 0.8888888889 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1.5 | 0.7231638418 | 0.8888888889 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300 | 0.7231638418 | 1.5 | 1.102941176 | 0.75 | Arching | Arching | Arching | Thermal Decomposition,corona
76 | 5092/2 | 50 MVA | 132/11.5 KV | BBL | 2009 | 8.4 | 130.2 | 15525.636 | 64733.676 | 169.176 | 2978.304 | 24.276 | 5 | 8 | 22 | 2.75 | 0.1864516129 | 1.6 | Arching | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 2.75 | 0.1864516129 | 1.6 | Discharge of Low Energy, | High Energy Discharge | Thermal Fault >700 c | 0.1864516129 | 2.75 | 0.9062448509 | 0.2272727273 | Arching | Arching | Arching | Arching
77 | 21327/1 | 16 MVA | 11/6.9 KV | VOLTAMP | 2009 | 8.2 | 5.658 | 15029.124 | 64151.224 | 155.308 | 1608.512 | 7.954 | 6 | 5.658 | 9 | 1.590668081 | 1.405797101 | 0.943 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 1.590668081 | 1.405797101 | 0.943 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.405797101 | 1.590668081 | 1.13150616 | 0.6666666667 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
78 | 21327/2 | 16 MVA | 11/6.9 KV | VOLTAMP | 2009 | 8.5 | 2.465 | 15773.62 | 66084.355 | 161.075 | 1835.405 | 9.18 | 11 | 9 | 6 | 0.6666666667 | 3.724137931 | 0.8181818182 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 0.6666666667 | 3.724137931 | 0.8181818182 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300 | 3.724137931 | 0.6666666667 | 0.6535947712 | 1.833333333 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
79 | 21327/3 | 16 MVA | 11/6.9 KV | VOLTAMP | 2010 | 8.5 | 6.375 | 16343.375 | 66314.365 | 124.355 | 1433.78 | 8.415 | 16 | 7 | 7 | 1 | 1.32 | 0.4375 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 1 | 1.32 | 0.4375 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300 | 1.32 | 1 | 0.8318478907 | 2.285714286 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
80 | 21327/4 | 16 MVA | 11/6.9 KV | VOLTAMP | 2010 | 8.3 | 7.304 | 15029.225 | 65325.648 | 136.535 | 1264.256 | 10.126 | 8 | 9 | 5 | 0.5555555556 | 1.386363636 | 1.125 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 0.5555555556 | 1.386363636 | 1.125 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.386363636 | 0.5555555556 | 0.4937783923 | 1.6 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
81 | 5104/5 | 50 MVA | 132/11 KV | BHARAT BIJLEE | 2009 | 7.8 | 14.43 | 14322.672 | 61768.356 | 92.274 | 919.698 | 6.708 | 14 | 6 | 8 | 1.333333333 | 0.4648648649 | 0.4285714286 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1.333333333 | 0.4648648649 | 0.4285714286 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300 | 0.4648648649 | 1.333333333 | 1.192605844 | 1.75 | Arching | Arching | Arching | Thermal Decomposition,corona
82 | 5104/7 | 50 MVA | 132/11 KV | BHARAT BIJLEE | 2009 | 7.5 | 19.35 | 13649.7 | 59061.75 | 107.55 | 1382.325 | 4.275 | 8.925 | 9 | 9 | 1 | 0.2209302326 | 1.008403361 | Arching | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 1 | 0.2209302326 | 1.008403361 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.2209302326 | 1 | 2.105263158 | 0.9916666667 | Arching | Arching | Arching | Thermal Decomposition,corona
83 | 5104/6 | 50 MVA | 132/11.5 KV | BHARAT BIJLEE | 2009 | 8.4 | 11.676 | 16229.304 | 65847.768 | 98.532 | 976.584 | 29.988 | 4.536 | 20.58 | 12 | 0.583090379 | 2.568345324 | 4.537037037 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Arching,Thermal Fault > 700 c | 0.583090379 | 2.568345324 | 4.537037037 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 2.568345324 | 0.583090379 | 0.400160064 | 0.378 | Thermal Decomposition, | Thermal Decomposition, | Arching | Arching
84 | 5105/2 | 50 MVA | 132/11.5 KV | BBL | 2009 | 8.3 | 16.932 | 15814.986 | 64855.702 | 115.536 | 1081.324 | 6.723 | 8 | 5.312 | 8 | 1.506024096 | 0.3970588235 | 0.664 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1.506024096 | 0.3970588235 | 0.664 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300 | 0.3970588235 | 1.506024096 | 1.189944965 | 1 | Arching | Arching | Arching | Thermal Decomposition,corona
85 | 5104/2 | 50 MVA | 132/11.5 KV | BHARAT BIJLEE | 2009 | 8 | 7.92 | 14483.28 | 63696.4 | 82.24 | 731.44 | 2.16 | 7 | 2.08 | 6 | 2.884615385 | 0.2727272727 | 0.2971428571 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 2.884615385 | 0.2727272727 | 0.2971428571 | Discharge of Low Energy, | High Energy Discharge | thermal fault <301 | 0.2727272727 | 2.884615385 | 2.777777778 | 1.166666667 | Arching | Arching | Arching | Thermal Decomposition,corona
86 | 5104/3 | 50 MVA | 132/11.5 KV | BHARAT BIJLEE | 2009 | 8.4 | 7.224 | 15828.96 | 66393.096 | 77.112 | 756.588 | 12.936 | 9 | 9 | 4 | 0.4444444444 | 1.790697674 | 1 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 0.4444444444 | 1.790697674 | 1 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <302 | 1.790697674 | 0.4444444444 | 0.3092145949 | 2.25 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
87 | 5105/1 | 50 MVA | 132/11.5 KV | BBL | 2009 | 8.6 | 8.514 | 16347.482 | 67521.094 | 177.504 | 1482.21 | 14.792 | 6 | 8 | 9 | 1.125 | 1.737373737 | 1.333333333 | Arching | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 1.125 | 1.737373737 | 1.333333333 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.737373737 | 1.125 | 0.608436993 | 0.6666666667 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
88 | HT-1756/2893 | 80 MVA | 132/11.5 KV | EMCO | 2008 | 8.5 | 4.845 | 16651.84 | 66801.585 | 88.995 | 858.84 | 8.16 | 5.865 | 7 | 8 | 1.142857143 | 1.684210526 | 1.193520887 | Arching | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 1.142857143 | 1.684210526 | 1.193520887 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.684210526 | 1.142857143 | 0.9803921569 | 0.733125 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
89 | HT-1756/2894 | 80 MVA | 132/11.5 KV | EMCO | 2008 | 8.2 | 4.264 | 15529.898 | 63413.47 | 214.266 | 1676.244 | 4.51 | 8 | 6 | 11 | 1.833333333 | 1.057692308 | 0.75 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 1.833333333 | 1.057692308 | 0.75 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.057692308 | 1.833333333 | 2.43902439 | 0.7272727273 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
90 | 2010305 | 50 MVA | 132/11 KV | BHEL | 1997 | 8.4 | 7.14 | 16665.684 | 64769.292 | 181.272 | 1550.892 | 7.896 | 9 | 9 | 12 | 1.333333333 | 1.105882353 | 1 | Arching | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 1.333333333 | 1.105882353 | 1 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.105882353 | 1.333333333 | 1.519756839 | 0.75 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
91 | 2010306 | 50 MVA | 132/11 KV | BHEL | 1997 | 8.2 | 1.23 | 15347.776 | 64312.026 | 172.364 | 1601.214 | 10.086 | 7 | 7 | 4 | 0.5714285714 | 8.2 | 1 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 0.5714285714 | 8.2 | 1 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 8.2 | 0.5714285714 | 0.3965893317 | 1.75 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
92 | 072ZM-003/01 | 50 MVA | 132/11.5 KV | KIRLOSKAR | 2008 | 8.6 | 2.838 | 16264.148 | 64729.964 | 235.898 | 3808.252 | 13.33 | 14 | 16.082 | 20 | 1.243626415 | 4.696969697 | 1.148714286 | Arching | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 1.243626415 | 4.696969697 | 1.148714286 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 4.696969697 | 1.243626415 | 1.500375094 | 0.7 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
93 | 5104/4 | 50 MVA | 132/11.5 KV | BHARAT BIJLEE | 2009 | 8.2 | 13.53 | 16380.976 | 62530.084 | 204.754 | 1704.698 | 6.806 | 9 | 9 | 8 | 0.8888888889 | 0.503030303 | 1 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.8888888889 | 0.503030303 | 1 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.503030303 | 0.8888888889 | 1.175433441 | 1.125 | Arching | Arching | Arching | Thermal Decomposition,corona
94 | 5104/1 | 50 MVA | 132/11.5 KV | BHARAT BIJLEE | 2009 | 8.1 | 13.041 | 15387.327 | 62300.502 | 202.986 | 2066.877 | 6.318 | 2.511 | 8 | 9 | 1.125 | 0.4844720497 | 3.185981681 | Arching | Arching,Low temprature thermal fault | Arching,Thermal Fault > 700 c | 1.125 | 0.4844720497 | 3.185981681 | Discharge of Low Energy, | High Energy Discharge | Thermal Fault >700 c | 0.4844720497 | 1.125 | 1.424501425 | 0.279 | Arching | Arching | Arching | Arching
95 | 21327/5 | 16 MVA | 11/6.9 KV | VOLTAMP | 2009 | 8.5 | 6.715 | 15889.135 | 67443.59 | 58.225 | 554.965 | 8.67 | 7 | 8.33 | 5 | 0.600240096 | 1.291139241 | 1.19 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 0.600240096 | 1.291139241 | 1.19 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.291139241 | 0.600240096 | 0.5767012687 | 1.4 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
96 | 21327/7 | 16 MVA | 11/6.9 KV | VOLTAMP | 2009 | 8.4 | 6.804 | 15326.052 | 66178.644 | 135.156 | 1290.408 | 6.3 | 16.884 | 34.104 | 6 | 0.1759324419 | 0.9259259259 | 2.019900498 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.1759324419 | 0.9259259259 | 2.019900498 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.9259259259 | 0.1759324419 | 0.9523809524 | 2.814 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
97 | 13133-01 | 90/120 MVA | 220/132 KV | ABB | 2014 | 8.4 | 1.596 | 16711.464 | 64650.18 | 139.02 | 1548.792 | 5 | 11 | 8 | 8 | 1 | 3.13283208 | 0.7272727273 | Arching | Low temperature thermal | Partial discharge, Normal | 1 | 3.13283208 | 0.7272727273 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 3.13283208 | 1 | 1.6 | 1.375 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
98 | 13146-01 | 90/120 MVA | 220/132 KV | ABB | 2017 | 8.6 | 1.376 | 16747.812 | 67333.614 | 93.568 | 932.154 | 8 | 22 | 3.784 | 13 | 3.43551797 | 5.813953488 | 0.172 | Arching | Low temperature thermal | Partial discharge, Normal | 3.43551797 | 5.813953488 | 0.172 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 5.813953488 | 3.43551797 | 1.625 | 1.692307692 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
99 | D-8305 | 11 MVA | 33/2.64 KV | AREVA | 2009 | 7.8 | 9.594 | 14368.458 | 60428.94 | 180.414 | 1991.496 | 6 | 14 | 9 | 7 | 0.7777777778 | 0.6253908693 | 0.6428571429 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Partial discharge, Normal | 0.7777777778 | 0.6253908693 | 0.6428571429 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.6253908693 | 0.7777777778 | 1.166666667 | 2 | Arching | Arching | Arching | Thermal Decomposition,corona
100 | B-30654 | 275 MVA | (420/√3)/21 KV | ALSTOM | 2013 | 7.9 | 1.817 | 15255.216 | 62242.125 | 34.918 | 406.376 | 8 | 7 | 2.523 | 9 | 3.567181926 | 4.40286186 | 0.3604285714 | Arching | Low temperature thermal | Partial discharge, Normal | 3.567181926 | 4.40286186 | 0.3604285714 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 4.40286186 | 3.567181926 | 1.125 | 0.7777777778 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
101 | B-30655 | 275 MVA | (420/√3)/21 KV | ALSTOM | 2013 | 8.2 | 4.182 | 15618.458 | 64543.922 | 42.148 | 592.368 | 9 | 9 | 5 | 5 | 1 | 2.152080344 | 0.5555555556 | Arching | Low temperature thermal | Partial discharge, Normal | 1 | 2.152080344 | 0.5555555556 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 2.152080344 | 1 | 0.5555555556 | 1.8 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
102 | B-30656 | 275 MVA | (420/√3)/21 KV | ALSTOM | 2013 | 7.8 | 2.964 | 14918.436 | 61339.278 | 45.084 | 532.662 | 7 | 7 | 8 | 5 | 0.625 | 2.361673414 | 1.142857143 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.625 | 2.361673414 | 1.142857143 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 2.361673414 | 0.625 | 0.7142857143 | 1.4 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
103 | B-30651 | 275 MVA | (420/√3)/11.5 KV | ALSTOM | 2012 | 8.2 | 2.214 | 15046.098 | 64905.952 | 90.856 | 975.39 | 9 | 5 | 8 | 3 | 0.375 | 4.06504065 | 1.6 | Partial discharge,Low Temprature thermal fault, | Low temperature thermal | Low Temprature thermal Fault,Thermal Fault<700c | 0.375 | 4.06504065 | 1.6 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 4.06504065 | 0.375 | 0.3333333333 | 1.666666667 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
104 | B-30657 | 275 MVA | (420/√3)/11.5 KV | ALSTOM | 2013 | 7.8 | 9 | 15479.88 | 61652.448 | 38.844 | 432.666 | 4 | 8 | 5.658 | 22 | 3.888299753 | 0.4444444444 | 0.70725 | Arching | Arching | Partial discharge, Normal | 3.888299753 | 0.4444444444 | 0.70725 | Discharge of Low Energy, | Discharge of flow of energy | thermal fault <300c | 0.4444444444 | 3.888299753 | 5.5 | 0.3636363636 | Arching | Arching | Arching | Arching
105 | B-30653 | 275 MVA | (420/√3)/11.5 KV | ALSTOM | 2012 | 8 | 7 | 15388.8 | 62948.96 | 47.12 | 551.44 | 2.56 | 9 | 9 | 8 | 0.8888888889 | 0.3657142857 | 1 | Partial discharge,Low Temprature thermal fault, | Arching | Low Temprature thermal Fault,Thermal Fault<700c | 0.8888888889 | 0.3657142857 | 1 | High Energy Discharge | Discharge of flow of energy | thermal fault <300c | 0.3657142857 | 0.8888888889 | 3.125 | 1.125 | Arching | Arching | Arching | Thermal Decomposition,corona
106 | 20104037TIG008-001 | 270 MVA | 765/22 KV | Hyundai | 2012 | 8.1 | 6.075 | 15392.025 | 63209.565 | 98.901 | 1174.662 | 4.131 | 5 | 7 | 5 | 0.7142857143 | 0.68 | 1.4 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.7142857143 | 0.68 | 1.4 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.68 | 0.7142857143 | 1.210360687 | 1 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
107 | 20104037TIG008-002 | 270 MVA | 765/22 KV | Hyundai | 2012 | 8.4 | 1.008 | 16335.228 | 65532.096 | 92.736 | 938.448 | 1.008 | 8 | 9 | 9 | 1 | 1 | 1.125 | Arching | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 1 | 1 | 1.125 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 1 | 1 | 8.928571429 | 0.8888888889 | Arching | Arching | Arching | Thermal Decomposition,corona
108 | 20104037TIG011-002 | 270 MVA | 765/22 KV | Hyundai | 2012 | 8.6 | 1.204 | 15808.434 | 67763.7 | 129.344 | 1359.402 | 1.032 | 9 | 6 | 4 | 0.6666666667 | 0.8571428571 | 0.6666666667 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Partial discharge, Normal | 0.6666666667 | 0.8571428571 | 0.6666666667 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.8571428571 | 0.6666666667 | 3.875968992 | 2.25 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
109 | 20104037TIG009-001 | 270 MVA | 765/22 KV | Hyundai | 2012 | 7.8 | 4.836 | 14574.612 | 61470.942 | 104.208 | 983.892 | 1.638 | 6 | 9 | 6 | 0.6666666667 | 0.3387096774 | 1.5 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.6666666667 | 0.3387096774 | 1.5 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.3387096774 | 0.6666666667 | 3.663003663 | 1 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
110 | 20104037TIG010-003 | 270 MVA | 765/22 KV | Hyundai | 2012 | 8.4 | 6.468 | 15166.62 | 66396.2964 | 125.328 | 1528.296 | 8 | 4 | 20.58 | 8 | 0.3887269193 | 1.23685838 | 5.145 | Partial discharge,Low Temprature thermal fault, | Low temperature thermal | Arching,Thermal Fault > 700 c | 0.3887269193 | 1.23685838 | 5.145 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.23685838 | 0.3887269193 | 1 | 0.5 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
111 | 20104037TIG013-001 | 270 MVA | 765/22 KV | Hyundai | 2012 | 8 | 4.4 | 14990.96 | 63142.16 | 118.16 | 1299.12 | 9 | 9 | 5.312 | 6 | 1.129518072 | 2.045454545 | 0.5902222222 | Arching | Low temperature thermal | Partial discharge, Normal | 1.129518072 | 2.045454545 | 0.5902222222 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 2.045454545 | 1.129518072 | 0.6666666667 | 1.5 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
112 | - | 270 MVA | 765/22 KV | Hyundai | 2012 | 8.2 | 1.312 | 14118.596 | 65043.712 | 133.414 | 1814.414 | 1.23 | 9 | 2.08 | 9 | 4.326923077 | 0.9375 | 0.2311111111 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 4.326923077 | 0.9375 | 0.2311111111 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.9375 | 4.326923077 | 7.317073171 | 1 | Arching | Arching | Arching | Thermal Decomposition,corona
113 | 20104037TIG013-004 | 270 MVA | 765/22 KV | Hyundai | 2012 | 8.5 | 2.72 | 16975.775 | 65470.91 | 127.33 | 1381.25 | 0.51 | 6 | 9 | 5 | 0.5555555556 | 0.1875 | 1.5 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.5555555556 | 0.1875 | 1.5 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.1875 | 0.5555555556 | 9.803921569 | 1.2 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
114 | 20104037TIG010-002 | 270 MVA | 765/22 KV | Hyundai | 2012 | 8.2 | 7.544 | 16442.148 | 63270.626 | 131.364 | 1652.628 | 4.428 | 9 | 8 | 8 | 1 | 0.5869565217 | 0.8888888889 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1 | 0.5869565217 | 0.8888888889 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.5869565217 | 1 | 1.806684734 | 1.125 | Arching | Arching | Arching | Thermal Decomposition,corona
115 | 20104037TIG004-001 | 270 MVA | 765/22 KV | Hyundai | 2012 | 8 | 1.92 | 15349.36 | 61935.52 | 157.84 | 1710.88 | 16.08 | 1.52 | 1.84 | 9 | 4.891304348 | 8.375 | 1.210526316 | Arching | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 4.891304348 | 8.375 | 1.210526316 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 8.375 | 4.891304348 | 0.5597014925 | 0.1688888889 | Thermal Decomposition, | Arching | Arching | Arching
116 | 20104037TIG004-003 | 270 MVA | 765/22 KV | Hyundai | 2012 | 7.9 | 2 | 15883.187 | 61018.652 | 104.517 | 1489.308 | 9 | 8 | 8 | 6 | 0.75 | 4.5 | 1 | Partial discharge,Low Temprature thermal fault, | Arching | Low Temprature thermal Fault,Thermal Fault<700c | 0.75 | 4.5 | 1 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 4.5 | 0.75 | 0.6666666667 | 1.333333333 | Thermal Decomposition, | FALSE | Arching | Thermal Decomposition,corona
117 | 20104037TIG004-004 | 270 MVA | 765/22 KV | Hyundai | 2012 | 7.9 | 1 | 15998.211 | 60882.535 | 102.305 | 1323.329 | 9.638 | 9 | 1.58 | 8 | 5.063291139 | 9.638 | 0.1755555556 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 5.063291139 | 9.638 | 0.1755555556 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | Partial Discharges, | 9.638 | 5.063291139 | 0.8300477277 | 1.125 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
118 | - | 270 MVA | 765/22 KV | Hyundai | 2011 | 8.4 | 3.192 | 15521.856 | 66827.04 | 100.044 | 960.12 | 6.132 | 9 | 9 | 4 | 0.4444444444 | 1.921052632 | 1 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 0.4444444444 | 1.921052632 | 1 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.921052632 | 0.4444444444 | 0.6523157208 | 2.25 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
119 | 20104037TIG011-003 | 270 MVA | 765/22 KV | Hyundai | 2011 | 8.2 | 1.148 | 15812.88 | 63793.868 | 112.996 | 1183.834 | 8.856 | 7 | 8 | 7 | 0.875 | 7.714285714 | 1.142857143 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 0.875 | 7.714285714 | 1.142857143 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 7.714285714 | 0.875 | 0.7904245709 | 1 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
120 | - | 270 MVA | 765/22 KV | Hyundai | 2011 | 8.5 | 5.525 | 16580.61 | 66042.11 | 129.115 | 1264.2815 | 9.35 | 8 | 6 | 4 | 0.6666666667 | 1.692307692 | 0.75 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 0.6666666667 | 1.692307692 | 0.75 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.692307692 | 0.6666666667 | 0.4278074866 | 2 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
121 | 20104037TIG013-002 | 270 MVA | 765/22 KV | Hyundai | 2011 | 7.6 | 6.536 | 14218.612 | 59415.052 | 120.004 | 1322.704 | 8.36 | 6 | 9 | 8 | 0.8888888889 | 1.279069767 | 1.5 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 0.8888888889 | 1.279069767 | 1.5 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.279069767 | 0.8888888889 | 0.956937799 | 0.75 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
122 | 20104037TIG009-003 | 270 MVA | 765/22 KV | Hyundai | 2011 | 7.3 | 1.387 | 14920.762 | 55917.051 | 109.208 | 1138.289 | 4.964 | 8 | 7 | 5 | 0.7142857143 | 3.578947368 | 0.875 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 0.7142857143 | 3.578947368 | 0.875 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 3.578947368 | 0.7142857143 | 1.007252216 | 1.6 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
123 | 20104037TIG010-001 | 270 MVA | 765/22 KV | Hyundai | 2011 | 7.6 | 6.46 | 14700.984 | 59265.408 | 132.392 | 1432.296 | 8.512 | 5 | 7 | 9 | 1.285714286 | 1.317647059 | 1.4 | Arching | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 1.285714286 | 1.317647059 | 1.4 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.317647059 | 1.285714286 | 1.057330827 | 0.5555555556 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
124 | TB1/621000174/2 | 16 MVA | 33/6.9 MVA | AREVA | 2010 | 8.5 | 7.225 | 15728.06 | 66868.565 | 117.47 | 1283.245 | 2.04 | 4 | 6 | 4 | 0.6666666667 | 0.2823529412 | 1.5 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.6666666667 | 0.2823529412 | 1.5 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.2823529412 | 0.6666666667 | 1.960784314 | 1 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
125 | TB1/621000174/1 | 16 MVA | 33/6.9 MVA | AREVA | 2010 | 8.7 | 9.309 | 16125.972 | 68530.422 | 126.411 | 1447.071 | 4.089 | 9 | 6 | 7 | 1.166666667 | 0.4392523364 | 0.6666666667 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1.166666667 | 0.4392523364 | 0.6666666667 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.4392523364 | 1.166666667 | 1.711910002 | 1.285714286 | Arching | Arching | Arching | Thermal Decomposition,corona
126 | 10000000021 | 10 MVA | 33/11 KV | PME | 2013 | 8.2 | 9.102 | 15283.652 | 63336.062 | 187.37 | 2234.664 | 11.808 | 108.65 | 29.93 | 99 | 3.307718009 | 1.297297297 | 0.2754716981 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 3.307718009 | 1.297297297 | 0.2754716981 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.297297297 | 3.307718009 | 8.384146341 | 1.097474747 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
127 | 172580 | 10 MVA | 33/11 KV | Rajasthan Transformers & Switchgears | 2006 | 8.4 | 3.948 | 15711.444 | 64968.708 | 228.648 | 2419.872 | 14.7 | 50.82 | 21.42 | 45 | 2.100840336 | 3.723404255 | 0.4214876033 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 2.100840336 | 3.723404255 | 0.4214876033 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 3.723404255 | 2.100840336 | 3.06122449 | 1.129333333 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
128 | ATL-81860703 | 10 MVA | 33/11 KV | Rajasthan Transformers & Switchgears | 2006 | 7.8 | 1.716 | 14555.19 | 60930.948 | 149.994 | 1546.272 | 27.222 | 22.152 | 232.83 | 224 | 0.9620753339 | 15.86363636 | 10.51056338 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Arching,Thermal Fault > 700 c | 0.9620753339 | 15.86363636 | 10.51056338 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 15.86363636 | 0.9620753339 | 8.228638601 | 0.09889285714 | Thermal Decomposition, | Arching | Arching | Arching
129 | Atl-838180809 | 10 MVA | 33/11 KV | Accurate Transformers Ltd | 2013 | 8.2 | 12.71 | 15477.992 | 62866.612 | 253.134 | 2793.576 | 13.038 | 61.91 | 11.562 | 55 | 4.756962463 | 1.025806452 | 0.1867549669 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 4.756962463 | 1.025806452 | 0.1867549669 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | Partial Discharges, | 1.025806452 | 4.756962463 | 4.218438411 | 1.125636364 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
130 | 2019003 | 16 MVA | 10.5/6.9 KV | BHEL | 2007 | 7.7 | 2.849 | 14016.772 | 61120.136 | 96.173 | 1131.746 | 1.617 | 7 | 2.772 | 8 | 2.886002886 | 0.5675675676 | 0.396 | Arching | Low temperature thermal | Partial discharge, Normal | 2.886002886 | 0.5675675676 | 0.396 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.5675675676 | 2.886002886 | 4.947433519 | 0.875 | Arching | Arching | Arching | Thermal Decomposition,corona
131 | 2019454 | 40 MVA | 220/33 KV | BHEL | 2008 | 8.3 | 1.743 | 15928.115 | 65784.721 | 57.353 | 734.716 | 9 | 8 | 8 | 45 | 5.625 | 5.163511188 | 1 | Arching | Low temperature thermal | Low Temprature thermal Fault,Thermal Fault<700c | 5.625 | 5.163511188 | 1 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 5.163511188 | 5.625 | 5 | 0.1777777778 | Thermal Decomposition, | Arching | Arching | Arching
132 | 2019455 | 40 MVA | 220/33 KV | BHEL | 2008 | 8.2 | 2.87 | 15284.226 | 65078.808 | 51.496 | 654.524 | 1.722 | 6 | 9 | 8 | 0.8888888889 | 0.6 | 1.5 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.8888888889 | 0.6 | 1.5 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.6 | 0.8888888889 | 4.645760743 | 0.75 | Arching | Arching | Arching | Thermal Decomposition,corona
133 | 2019004 | 16 MVA | 10.5/6.9 KV | BHEL | 2007 | 8.1 | 3.645 | 14967.423 | 64262.808 | 83.511 | 974.268 | 2.187 | 9 | 7.209 | 9 | 1.248439451 | 0.6 | 0.801 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1.248439451 | 0.6 | 0.801 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.6 | 1.248439451 | 4.115226337 | 1 | Arching | Arching | Arching | Thermal Decomposition,corona
134 | 6005784 | 50/75/130 MVA | 220/132 KV | BHEL | 1999 | 7.9 | 7.821 | 14860.216 | 61889.943 | 154.208 | 1565.148 | 5.214 | 1.185 | 3.634 | 5 | 1.375894331 | 0.6666666667 | 3.066666667 | Arching | Arching,Low temprature thermal fault | Arching,Thermal Fault > 700 c | 1.375894331 | 0.6666666667 | 3.066666667 | Discharge of Low Energy, | High Energy Discharge | Thermal Fault >700 c | 0.6666666667 | 1.375894331 | 0.9589566552 | 0.237 | Arching | Arching | Arching | Arching
135 | 6005784 | 50/75/130 MVA | 220/132 KV | BHEL | 1999 | 8.1 | 23.328 | 14663.025 | 63413.928 | 162.972 | 1702.782 | 6.804 | 4.698 | 3.483 | 6 | 1.722652885 | 0.2916666667 | 0.7413793103 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1.722652885 | 0.2916666667 | 0.7413793103 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.2916666667 | 1.722652885 | 0.8818342152 | 0.783 | Arching | Arching | Arching | Thermal Decomposition,corona
136 | 6005784 | 50/75/130 MVA | 220/132 KV | BHEL | 1999 | 7.9 | 10.586 | 15856.643 | 60644.824 | 126.321 | 1406.358 | 4.898 | 6.241 | 3.634 | 7 | 1.926252064 | 0.4626865672 | 0.582278481 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1.926252064 | 0.4626865672 | 0.582278481 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.4626865672 | 1.926252064 | 1.429154757 | 0.8915714286 | Arching | Arching | Arching | Thermal Decomposition,corona
137 | 6005784 | 50/75/130 MVA | 220/132 KV | BHEL | 1999 | 8 | 12.72 | 15047.04 | 62522.64 | 118.48 | 1264.16 | 4.96 | 5.92 | 3.28 | 7 | 2.134146341 | 0.3899371069 | 0.5540540541 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 2.134146341 | 0.3899371069 | 0.5540540541 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.3899371069 | 2.134146341 | 1.411290323 | 0.8457142857 | Arching | Arching | Arching | Thermal Decomposition,corona
138 | 6005785 | 50/75/130 MVA | 220/132 KV | BHEL | 1999 | 8.4 | 5.46 | 15844.164 | 65701.692 | 162.372 | 1727.124 | 4.116 | 12 | 8 | 7 | 0.875 | 0.7538461538 | 0.6666666667 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Partial discharge, Normal | 0.875 | 0.7538461538 | 0.6666666667 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.7538461538 | 0.875 | 1.700680272 | 1.714285714 | Arching | Arching | Arching | Thermal Decomposition,corona
139 | 6005785 | 50/75/130 MVA | 220/132 KV | BHEL | 1999 | 7.9 | 15.484 | 14720.307 | 61508.847 | 164.794 | 1734.445 | 5.135 | 4 | 9 | 8 | 0.8888888889 | 0.3316326531 | 2.25 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.8888888889 | 0.3316326531 | 2.25 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.3316326531 | 0.8888888889 | 1.557935735 | 0.5 | Arching | Arching | Arching | Thermal Decomposition,corona
140 | 6005785 | 50/75/130 MVA | 220/132 KV | BHEL | 1999 | 8.2 | 26.978 | 15334.902 | 63969.84 | 116.522 | 1319.134 | 3.198 | 67 | 7 | 5 | 0.7142857143 | 0.1185410334 | 0.1044776119 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Partial discharge, Normal | 0.7142857143 | 0.1185410334 | 0.1044776119 | High Energy Discharge | High Energy Discharge | Partial Discharges, | 0.1185410334 | 0.7142857143 | 1.563477173 | 13.4 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
141 | 6005785 | 50/75/130 MVA | 220/132 KV | BHEL | 1999 | 8.5 | 17.34 | 16984.445 | 65375.795 | 128.69 | 1359.15 | 6.375 | 8 | 5 | 9 | 1.8 | 0.3676470588 | 0.625 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1.8 | 0.3676470588 | 0.625 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.3676470588 | 1.8 | 1.411764706 | 0.8888888889 | Arching | Arching | Arching | Thermal Decomposition,corona
142 | B-29508 | 50/75/130 MVA | 220/132 KV | ALSTOM | 1999 | 7.9 | 5.925 | 14321.041 | 62576.611 | 133.194 | 1426.108 | 3.081 | 9 | 4 | 7 | 1.75 | 0.52 | 0.4444444444 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1.75 | 0.52 | 0.4444444444 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.52 | 1.75 | 2.271989614 | 1.285714286 | Arching | Arching | Arching | Thermal Decomposition,corona
143 | B-29508 | 50/75/130 MVA | 220/132 KV | ALSTOM | 1999 | 8.3 | 17.264 | 15936.083 | 64897.285 | 107.651 | 1124.982 | 5.063 | 8 | 8 | 4 | 0.5 | 0.2932692308 | 1 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.5 | 0.2932692308 | 1 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.2932692308 | 0.5 | 0.7900454276 | 2 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
144 | B-29508 | 50/75/130 MVA | 220/132 KV | ALSTOM | 1999 | 8.1 | 13.365 | 16511.688 | 62451.567 | 111.699 | 1364.931 | 6.399 | 9 | 6 | 3 | 0.5 | 0.4787878788 | 0.6666666667 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Partial discharge, Normal | 0.5 | 0.4787878788 | 0.6666666667 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.4787878788 | 0.5 | 0.4688232536 | 3 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
145 | B-29508 | 50/75/130 MVA | 220/132 KV | ALSTOM | 1999 | 8.3 | 7.553 | 17032.762 | 63263.43 | 141.598 | 1648.131 | 2.905 | 6 | 4 | 8 | 2 | 0.3846153846 | 0.6666666667 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 2 | 0.3846153846 | 0.6666666667 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.3846153846 | 2 | 2.753872633 | 0.75 | Arching | Arching | Arching | Thermal Decomposition,corona
146 | B-29509 | 50/75/130 MVA | 220/132 KV | ALSTOM | 1999 | 8.2 | 7.298 | 14403.382 | 64648.472 | 165.804 | 1724.46 | 4.838 | 8 | 4 | 6 | 1.5 | 0.6629213483 | 0.5 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1.5 | 0.6629213483 | 0.5 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.6629213483 | 1.5 | 1.240181893 | 1.333333333 | Arching | Arching | Arching | Thermal Decomposition,corona
147 | B-29509 | 50/75/130 MVA | 220/132 KV | ALSTOM | 1999 | 7.8 | 4.836 | 14480.778 | 61363.536 | 142.584 | 1502.592 | 5 | 6 | 8 | 8 | 1 | 1.033912324 | 1.333333333 | Arching | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 1 | 1.033912324 | 1.333333333 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.033912324 | 1 | 1.6 | 0.75 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
148 | B-29509 | 50/75/130 MVA | 220/132 KV | ALSTOM | 1999 | 8.2 | 16.81 | 17073.712 | 62559.03 | 152.192 | 1617.614 | 5.084 | 5 | 4.182 | 9 | 2.152080344 | 0.3024390244 | 0.8364 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 2.152080344 | 0.3024390244 | 0.8364 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.3024390244 | 2.152080344 | 1.770259638 | 0.5555555556 | Arching | Arching | Arching | Thermal Decomposition,corona
149 | B-29509 | 50/75/130 MVA | 220/132 KV | ALSTOM | 1999 | 7.9 | 15.247 | 16330.406 | 60114.339 | 177.276 | 1726.229 | 3.081 | 5 | 2.291 | 6 | 2.618943693 | 0.2020725389 | 0.4582 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 2.618943693 | 0.2020725389 | 0.4582 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.2020725389 | 2.618943693 | 1.947419669 | 0.8333333333 | Arching | Arching | Arching | Thermal Decomposition,corona
150 | BH8791/4 | 40 MVA | 220/11 KV | CGL | 2001 | 7.9 | 5.451 | 15377.35 | 60835.451 | 191.654 | 2103.612 | 7.821 | 2.686 | 4 | 8 | 2 | 1.434782609 | 1.489203276 | Arching | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 2 | 1.434782609 | 1.489203276 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.434782609 | 2 | 1.022887099 | 0.33575 | Thermal Decomposition, | Arching | Arching | Arching
151 | BH8791/5 | 40 MVA | 220/11 KV | ALSTOM | 2001 | 7.8 | 6.864 | 15875.34 | 59400.51 | 163.566 | 1740.258 | 8.502 | 4.758 | 5 | 8 | 1.6 | 1.238636364 | 1.050861707 | Arching | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 1.6 | 1.238636364 | 1.050861707 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.238636364 | 1.6 | 0.9409550694 | 0.59475 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
152 | BH8791/3 | 40 MVA | 220/11 KV | CGL | 2001 | 8.1 | 7.371 | 15544.305 | 61775.865 | 210.276 | 2278.044 | 13.203 | 5.589 | 7 | 8 | 1.142857143 | 1.791208791 | 1.25246019 | Arching | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 1.142857143 | 1.791208791 | 1.25246019 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.791208791 | 1.142857143 | 0.6059228963 | 0.698625 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
153 | 092Y0003/01 | 40 MVA | 220/11 KV | KIRLOSKER | 2003 | 8.3 | 10.375 | 15938.241 | 63449.682 | 256.553 | 2676.335 | 8.217 | 2.075 | 8 | 11 | 1.375 | 0.792 | 3.855421687 | Arching | Arching,Low temprature thermal fault | Arching,Thermal Fault > 700 c | 1.375 | 0.792 | 3.855421687 | Discharge of Low Energy, | High Energy Discharge | Thermal Fault >700 c | 0.792 | 1.375 | 1.338688086 | 0.1886363636 | Arching | Arching | Arching | Arching
154 | 29758 | 40 MVA | 220/11 KV | ALSTOM | 2003 | 8.2 | 7.872 | 16914.222 | 61759.858 | 183.352 | 2462.296 | 1.558 | 4 | 5 | 9 | 1.8 | 0.1979166667 | 1.25 | Arching | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 1.8 | 0.1979166667 | 1.25 | Discharge of Low Energy, | High Energy Discharge | Thermal Fault >700 c | 0.1979166667 | 1.8 | 5.776636714 | 0.4444444444 | Arching | Arching | Arching | Thermal Decomposition,corona
155 | 20161629 | 40 MVA | 220/11 KV | BHEL | 2004 | 8.1 | 12.231 | 16851.321 | 61180.92 | 211.491 | 2129.733 | 4.212 | 7 | 3 | 9 | 3 | 0.3443708609 | 0.4285714286 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 3 | 0.3443708609 | 0.4285714286 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.3443708609 | 3 | 2.136752137 | 0.7777777778 | Arching | Arching | Arching | Thermal Decomposition,corona
156 | 2015970 | 40 MVA | 230/11 KV | BHEL | 2004 | 8 | 80.64 | 16589.28 | 60878.16 | 120.88 | 1351.28 | 7.2 | 9 | 8 | 4 | 0.5 | 0.08928571429 | 0.8888888889 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Partial discharge, Normal | 0.5 | 0.08928571429 | 0.8888888889 | High Energy Discharge | Partial Discharges, | thermal fault <300c | 0.08928571429 | 0.5 | 0.5555555556 | 2.25 | Corona,Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
157 | 2015969 | 40 MVA | 230/11 KV | BHEL | 2004 | 8.1 | 5.022 | 15642.639 | 62309.736 | 195.291 | 1904.472 | 5.265 | 3.888 | 5 | 8 | 1.6 | 1.048387097 | 1.28600823 | Arching | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 1.6 | 1.048387097 | 1.28600823 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.048387097 | 1.6 | 1.519468186 | 0.486 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
158 | 8791/1 | 40 MVA | 230/11 KV | CGL | 2011 | 7.8 | 7.488 | 15555.852 | 59425.548 | 185.796 | 1665.768 | 4.212 | 3.822 | 9 | 3 | 0.3333333333 | 0.5625 | 2.354788069 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.3333333333 | 0.5625 | 2.354788069 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.5625 | 0.3333333333 | 0.7122507123 | 1.274 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
159 | 2016865 | 25 MVA | 33/6.9 KV | BHEL | 2004 | 8.2 | 30.012 | 16854.526 | 62275.556 | 164.574 | 1836.226 | 4.592 | 8 | 5 | 0 | 0 | 0.1530054645 | 0.625 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Partial discharge, Normal | 0 | 0.1530054645 | 0.625 | Thermal Fault> 300c and<700 c | High Energy Discharge | thermal fault <300c | 0.1530054645 | 0 | 0 |  | Arching | Thermal Decomposition, | Thermal Decomposition,corona | Thermal Decomposition,corona
160 | 2017091 | 25 MVA | 33/6.9 KV | BHEL | 2005 | 7.9 | 7.584 | 15728.347 | 59686.633 | 211.799 | 2372.449 | 3.713 | 9 | 6 | 9 | 1.5 | 0.4895833333 | 0.6666666667 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1.5 | 0.4895833333 | 0.6666666667 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.4895833333 | 1.5 | 2.423915971 | 1 | Arching | Arching | Arching | Thermal Decomposition,corona
161 | 08ZG-014/01 | 25 MVA | 33/6.9 KV | KIRLOSKER | 2008 | 8.3 | 17.264 | 17081.981 | 61550.144 | 194.967 | 2986.506 | 10.458 | 4.648 | 8 | 6 | 0.75 | 0.6057692308 | 1.721170396 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.75 | 0.6057692308 | 1.721170396 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.6057692308 | 0.75 | 0.5737234653 | 0.7746666667 | Arching | FALSE | Arching | Thermal Decomposition,corona
162 | 2016864 | 25 MVA | 33/6.9 KV | BHEL | 2004 | 8 | 6.08 | 15352.4 | 62206.96 | 123.6 | 1375.44 | 4.48 | 3.84 | 5 | 8 | 1.6 | 0.7368421053 | 1.302083333 | Arching | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 1.6 | 0.7368421053 | 1.302083333 | Discharge of Low Energy, | High Energy Discharge | Thermal Fault >700 c | 0.7368421053 | 1.6 | 1.785714286 | 0.48 | Arching | Arching | Arching | Thermal Decomposition,corona
163 | 05ZG-007/01 | 25 MVA | 33/6.6 KV | KIRLOSKER | NA | 8.5 | 22.015 | 16761.32 | 63918.725 | 160.565 | 1917.43 | 301.58 | 276.93 | 1049.24 | 5555 | 5.294308261 | 13.6988417 | 3.788827502 | Arching | Thermal Fault <700c, thermal fault >700c | Arching,Thermal Fault > 700 c | 5.294308261 | 13.6988417 | 3.788827502 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 13.6988417 | 5.294308261 | 18.41965648 | 0.04985238524 | Thermal Decomposition, | Arching | Arching | Arching
164 | 05ZG-007/02 | 25 MVA | 33/6.6 KV | KIRLOSKER | NA | 8.1 | 8.019 | 15627.492 | 62761.473 | 153.981 | 1666.008 | 3.888 | 5.589 | 4 | 9 | 2.25 | 0.4848484848 | 0.7156915369 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 2.25 | 0.4848484848 | 0.7156915369 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.4848484848 | 2.25 | 2.314814815 | 0.621 | Arching | Arching | Arching | Thermal Decomposition,corona
165 | NA | 15 MVA | 33/11.5 KV | NA | NA | 7.9 | 11.455 | 15188.382 | 61537.366 | 154.524 | 1663.582 | 9.559 | 9 | 4 | 6 | 1.5 | 0.8344827586 | 0.4444444444 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1.5 | 0.8344827586 | 0.4444444444 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.8344827586 | 1.5 | 0.6276807197 | 1.5 | Arching | Arching | Arching | Thermal Decomposition,corona
166 | NA | 15 MVA | 33/11.5 KV | NA | NA | 8.2 | 20.828 | 16161.79 | 62867.514 | 152.356 | 1714.702 | 11.316 | 3.936 | 10.086 | 12 | 1.189767995 | 0.5433070866 | 2.5625 | Arching | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 1.189767995 | 0.5433070866 | 2.5625 | Discharge of Low Energy, | High Energy Discharge | Thermal Fault >700 c | 0.5433070866 | 1.189767995 | 1.060445387 | 0.328 | Arching | Arching | Arching | Arching
167 | NA | 15 MVA | 33/11.5 KV | NA | NA | 7.6 | 10.564 | 16010.16 | 56431.596 | 217.056 | 2891.952 | 12.312 | 2.052 | 8 | 777 | 97.125 | 1.165467626 | 3.898635478 | Arching | Thermal Fault <700c, thermal fault >700c | Arching,Thermal Fault > 700 c | 97.125 | 1.165467626 | 3.898635478 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.165467626 | 97.125 | 63.10916179 | 0.002640926641 | Thermal Decomposition, | Arching | Arching | Arching
168 | D-6893 | 10 MVA | 33/6.6 KV | AREVA | 2006 | 7.3 | 220.387 | 13321.332 | 56336.071 | 137.532 | 1411.674 | 106.507 | 20.294 | 129.794 | 614.222 | 4.732283465 | 0.4832726068 | 6.395683453 | Arching | Arching,Low temprature thermal fault | Arching,Thermal Fault > 700 c | 4.732283465 | 0.4832726068 | 6.395683453 | Discharge of Low Energy, | High Energy Discharge | Thermal Fault >700 c | 0.4832726068 | 4.732283465 | 5.766963674 | 0.03304017114 | Arching | Arching | Arching | Arching
169 | D-6893 | 10 MVA | 33/6.6 KV | AREVA | 2006 | 8.5 | 70.465 | 16554.43 | 65577.755 | 83.725 | 968.66 | 31.28 | 4.505 | 121.635 | 826.71 | 6.796645702 | 0.4439083233 | 27 | Arching | Arching,Low temprature thermal fault | Arching,Thermal Fault > 700 c | 6.796645702 | 0.4439083233 | 27 | Discharge of Low Energy, | High Energy Discharge | Thermal Fault >700 c | 0.4439083233 | 6.796645702 | 26.42934783 | 0.005449311125 | Arching | Arching | Arching | Arching
170 | 2044052 | 50/75/150 MVA | 220/132 KV | BHEL | 2018 | 7.5 | 8.4 | 13868.775 | 59577.225 | 96.6 | 1034.475 | 9 | 6 | 4 | 7 | 1.75 | 1.071428571 | 0.6666666667 | Arching | Low temperature thermal | Partial discharge, Normal | 1.75 | 1.071428571 | 0.6666666667 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.071428571 | 1.75 | 0.7777777778 | 0.8571428571 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
171 | 2044052 | 50/75/150 MVA | 220/132 KV | BHEL | 2018 | 7.5 | 11.925 | 13730.625 | 59645.475 | 116.775 | 1047.45 | 2.85 | 7 | 5 | 7 | 1.4 | 0.2389937107 | 0.7142857143 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1.4 | 0.2389937107 | 0.7142857143 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.2389937107 | 1.4 | 2.456140351 | 1 | Arching | Arching | Arching | Thermal Decomposition,corona
172 | 2044052 | 50/75/150 MVA | 220/132 KV | BHEL | 2018 | 7.8 | 0.78 | 17048.382 | 59947.134 | 66.69 | 544.986 | 6 | 8 | 6 | 8 | 1.333333333 | 7.692307692 | 0.75 | Arching | Low temperature thermal | Partial discharge, Normal | 1.333333333 | 7.692307692 | 0.75 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 7.692307692 | 1.333333333 | 1.333333333 | 1 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
173 | 2044052 | 50/75/150 MVA | 220/132 KV | BHEL | 2018 | 7.6 | 0.76 | 15901.784 | 58674.66 | 57.988 | 530.556 | 9 | 6 | 7 | 5 | 0.7142857143 | 11.84210526 | 1.166666667 | Partial discharge,Low Temprature thermal fault, | Low temperature thermal | Low Temprature thermal Fault,Thermal Fault<700c | 0.7142857143 | 11.84210526 | 1.166666667 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 11.84210526 | 0.7142857143 | 0.5555555556 | 1.2 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
174 | 2044053 | 50/75/150 MVA | 220/132 KV | BHEL | 2017 | 8.3 | 13.695 | 16630.295 | 64189.046 | 96.197 | 1172.292 | 4.648 | 4 | 8 | 9 | 1.125 | 0.3393939394 | 2 | Arching | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 1.125 | 0.3393939394 | 2 | Discharge of Low Energy, | High Energy Discharge | Thermal Fault >700 c | 0.3393939394 | 1.125 | 1.936316695 | 0.4444444444 | Arching | Arching | Arching | Thermal Decomposition,corona
175 | 2044053 | 50/75/150 MVA | 220/132 KV | BHEL | 2017 | 7.9 | 40.685 | 14924.522 | 61763.543 | 173.642 | 1644.069 | 7.584 | 6 | 9 | 7 | 0.7777777778 | 0.186407767 | 1.5 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.7777777778 | 0.186407767 | 1.5 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.186407767 | 0.7777777778 | 0.9229957806 | 0.8571428571 | Arching | Arching | Arching | Thermal Decomposition,corona
176 | 2044053 | 50/75/150 MVA | 220/132 KV | BHEL | 2017 | 8.2 | 44.936 | 16620.252 | 62920.322 | 181.63 | 1723.722 | 5.33 | 3.936 | 5 | 4 | 0.8 | 0.1186131387 | 1.270325203 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.8 | 0.1186131387 | 1.270325203 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.1186131387 | 0.8 | 0.7504690432 | 0.984 | Arching | Arching | Arching | Thermal Decomposition,corona
177 | 2044053 | 50/75/150 MVA | 220/132 KV | BHEL | 2017 | 8.3 | 62.582 | 16012.443 | 64309.147 | 224.847 | 1955.646 | 6.225 | 5.395 | 6 | 7 | 1.166666667 | 0.09946949602 | 1.112140871 | Arching | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 1.166666667 | 0.09946949602 | 1.112140871 | Discharge of Low Energy, | Partial Discharges, | Thermal Fault >700 c | 0.09946949602 | 1.166666667 | 1.124497992 | 0.7707142857 | Corona,Arching | Arching | Arching | Thermal Decomposition,corona
178 | JN-3166/2 | 26.5 MVA | 33/6.6KV | VOLTAMP | 1994 | 8 | 42.64 | 15244.32 | 61478.4 | 177.04 | 1943.6 | 96.08 | 192.4 | 7.92 | 7 | 0.8838383838 | 2.253283302 | 0.04116424116 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 0.8838383838 | 2.253283302 | 0.04116424116 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Partial Discharges, | 2.253283302 | 0.8838383838 | 0.07285595337 | 27.48571429 | Thermal Decomposition, | Arching | Thermal Decomposition,corona | Thermal Decomposition,corona
179 | TBI/623000451/2 | 16 MVA | 33/6.9 KV | SCHNEIDER ELECTRIC | 2012 | 8.2 | 20.828 | 15354.746 | 62647.918 | 229.026 | 2546.018 | 150.224 | 56.17 | 209.51 | 155 | 0.7398214882 | 7.212598425 | 3.729927007 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Arching,Thermal Fault > 700 c | 0.7398214882 | 7.212598425 | 3.729927007 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 7.212598425 | 0.7398214882 | 1.031792523 | 0.3623870968 | Thermal Decomposition, | Thermal Decomposition, | Arching | Arching
180 | 23170 | 10 MVA | 33/6.6 KV | C Parksion | -- | 7.6 | 12.844 | 14590.024 | 58980.028 | 147.06 | 1503.66 | 9 | 6 | 8 | 5 | 0.625 | 0.7007162878 | 1.333333333 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.625 | 0.7007162878 | 1.333333333 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.7007162878 | 0.625 | 0.5555555556 | 1.2 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
181 | 7644/1 | 11 MVA | -- | CGL | 2013 | 8.1 | 4.212 | 16159.662 | 62126.109 | 118.665 | 1390.689 | 2.511 | 9 | 6 | 9 | 1.5 | 0.5961538462 | 0.6666666667 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1.5 | 0.5961538462 | 0.6666666667 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.5961538462 | 1.5 | 3.584229391 | 1 | Arching | Arching | Arching | Thermal Decomposition,corona
182 | 680800360 | 16/20 MVA | 66/6.6 KV | AREVA | 2008 | 7.8 | 12.09 | 14453.634 | 61692.15 | 128.154 | 1368.744 | 0.936 | 5 | 9 | 7 | 0.7777777778 | 0.07741935484 | 1.8 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.7777777778 | 0.07741935484 | 1.8 | High Energy Discharge | Partial Discharges, | Thermal Fault >700 c | 0.07741935484 | 0.7777777778 | 7.478632479 | 0.7142857143 | Corona,Arching | Arching | Arching | Thermal Decomposition,corona
183 | 1221636 | 16/20 MVA | 66/6.6 KV | AREVA | 2013 | 8 | 30.88 | 15289.92 | 63292.16 | 52.4 | 604.08 | 28.48 | 18.24 | 71.92 | 176 | 2.447163515 | 0.9222797927 | 3.942982456 | Arching | Arching,Low temprature thermal fault | Arching,Thermal Fault > 700 c | 2.447163515 | 0.9222797927 | 3.942982456 | Discharge of Low Energy, | High Energy Discharge | Thermal Fault >700 c | 0.9222797927 | 2.447163515 | 6.179775281 | 0.1036363636 | Arching | Arching | Arching | Arching
184 | 12054-1 | 80 MVA | 141.2/35.3 KV | ABB | 2008 | 8.1 | 12.555 | 16728.201 | 61966.701 | 116.964 | 1233.954 | 2.916 | 12 | 9 | 4 | 0.4444444444 | 0.2322580645 | 0.75 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Partial discharge, Normal | 0.4444444444 | 0.2322580645 | 0.75 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.2322580645 | 0.4444444444 | 1.371742112 | 3 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
185 | 12043-2 | 80 MVA | 141.2/35.3 KV | ABB | 2006 | 7.6 | 6.688 | 14018.276 | 59203.924 | 144.324 | 1553.212 | 7.448 | 1.596 | 4 | 6 | 1.5 | 1.113636364 | 2.506265664 | Arching | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 1.5 | 1.113636364 | 2.506265664 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.113636364 | 1.5 | 0.8055853921 | 0.266 | Thermal Decomposition, | Arching | Arching | Arching
186 | 12043-3 | 80 MVA | 141.2/35.3 KV | ABB | 2006 | 8 | 2.64 | 15906.8 | 61196.64 | 157.44 | 1698.72 | 5.04 | 11 | 7 | 4 | 0.5714285714 | 1.909090909 | 0.6363636364 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 0.5714285714 | 1.909090909 | 0.6363636364 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.909090909 | 0.5714285714 | 0.7936507937 | 2.75 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
187 | 130145-2 | 80 MVA | 63000/8000 V | TELK | 2003 | 7.7 | 7.007 | 15410.395 | 59954.818 | 101.794 | 1118.271 | 4.851 | 14 | 7 | 6 | 0.8571428571 | 0.6923076923 | 0.5 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Partial discharge, Normal | 0.8571428571 | 0.6923076923 | 0.5 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.6923076923 | 0.8571428571 | 1.23685838 | 2.333333333 | Arching | Arching | Arching | Thermal Decomposition,corona
188 | 130145-3 | 80 MVA | 63000/8000 V | TELK | 2003 | 7.6 | 2.052 | 15628.336 | 58494.236 | 116.052 | 961.932 | 1.444 | 15 | 4 | 4 | 1 | 0.7037037037 | 0.2666666667 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1 | 0.7037037037 | 0.2666666667 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.7037037037 | 1 | 2.770083102 | 3.75 | Arching | Arching | Arching | Thermal Decomposition,corona
189 | 130145-4 | 80 MVA | 63000/8000 V | TELK | 2003 | 7.8 | 4.368 | 15768.87 | 59983.482 | 109.044 | 1208.61 | 1.638 | 7 | 7 | 3 | 0.4285714286 | 0.375 | 1 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.4285714286 | 0.375 | 1 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.375 | 0.4285714286 | 1.831501832 | 2.333333333 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
190 | M-6037 | 10 MVA | 33/6.6 KV | CGL | 1997 | 7.9 | 2.844 | 14320.883 | 62104.744 | 150.258 | 1674.721 | 9 | 9 | 9 | 6 | 0.6666666667 | 3.164556962 | 1 | Partial discharge,Low Temprature thermal fault, | Low temperature thermal | Low Temprature thermal Fault,Thermal Fault<700c | 0.6666666667 | 3.164556962 | 1 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 3.164556962 | 0.6666666667 | 0.6666666667 | 1.5 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
191 | SAP-10041067 | 15 MVA | 33/6.6 KV | -- | 1936 | 8.3 | 4.648 | 14571.48 | 64508.098 | 233.313 | 2462.776 | 8.134 | 9 | 9.296 | 7 | 0.7530120482 | 1.75 | 1.032888889 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 0.7530120482 | 1.75 | 1.032888889 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.75 | 0.7530120482 | 0.8605851979 | 1.285714286 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
192 | 93XG-004/06 | 16 MVA | 33/11/6.6 KV | KIRLOSKAR | 1995 | 7.6 | 136.648 | 15916.452 | 55961.232 | 150.936 | 1691.152 | 176.244 | 11.704 | 330.98 | 541.272 | 1.635361653 | 1.289766407 | 28.27922078 | Arching | Thermal Fault <700c, thermal fault >700c | Arching,Thermal Fault > 700 c | 1.635361653 | 1.289766407 | 28.27922078 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.289766407 | 1.635361653 | 3.071151358 | 0.02162313957 | Thermal Decomposition, | Arching | Arching | Arching
193 | TO9548/1 | 80 MVA | 141.2/35.3 KV | CGL | 2009 | 7.6 | 1.9 | 14074.592 | 60269.596 | 105.564 | 951.748 | 1.596 | 8 | 6 | 8 | 1.333333333 | 0.84 | 0.75 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1.333333333 | 0.84 | 0.75 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.84 | 1.333333333 | 5.012531328 | 1 | Arching | Arching | Arching | Thermal Decomposition,corona
194 | TO9548/2 | 80 MVA | 141.2/35.3 KV | CGL | 2009 | 8.1 | 4.941 | 14670.153 | 64408.77 | 125.388 | 1315.359 | 1.134 | 9 | 2 | 6 | 3 | 0.2295081967 | 0.2222222222 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 3 | 0.2295081967 | 0.2222222222 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.2295081967 | 3 | 5.291005291 | 1.5 | Arching | Arching | Arching | Thermal Decomposition,corona
195 | TO9548/3 | 80 MVA | 141.2/35.3 KV | CGL | 2009 | 7.8 | 6.552 | 15694.224 | 60615.828 | 127.062 | 1125.15 | 4.134 | 6 | 8 | 4 | 0.5 | 0.630952381 | 1.333333333 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.5 | 0.630952381 | 1.333333333 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.630952381 | 0.5 | 0.9675858732 | 1.5 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
196 | 12067-001 | 80 MVA | 141.2/35.3 KV | ABB | 2010 | 8.2 | 2.378 | 16191.966 | 63539.258 | 80.524 | 1141.768 | 1.558 | 4 | 2.46 | 3 | 1.219512195 | 0.6551724138 | 0.615 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1.219512195 | 0.6551724138 | 0.615 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.6551724138 | 1.219512195 | 1.925545571 | 1.333333333 | Arching | Arching | Arching | Thermal Decomposition,corona
197 | 12067-002 | 80 MVA | 141.2/35.3 KV | ABB | 2010 | 7.6 | 4.94 | 14763.304 | 59249.98 | 93.632 | 959.804 | 1.064 | 3 | 9 | 9 | 1 | 0.2153846154 | 3 | Arching | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 1 | 0.2153846154 | 3 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.2153846154 | 1 | 8.458646617 | 0.3333333333 | Arching | Arching | Arching | Arching
198 | 16460 | 85 | 11000 | EMCO LTD., | 2010 | 8.8 | 8.448 | 18471.816 | 65440.76 | 216.128 | 2844.688 | 19.096 | 13.2 | 27.632 | 33 | 1.194267516 | 2.260416667 | 2.093333333 | Arching | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 1.194267516 | 2.260416667 | 2.093333333 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 2.260416667 | 1.194267516 | 1.728110599 | 0.4 | Thermal Decomposition, | Arching | Arching | FALSE
199 | D-6893 | 10 MVA | 33/6.6 KV | AREVA | 2006 | 7.6 | 145.312 | 13909.824 | 59298.62 | 146.3 | 1569.02 | 65.284 | 13.528 | 51.528 | 183.464 | 3.560471976 | 0.4492677824 | 3.808988764 | Arching | Arching,Low temprature thermal fault | Arching,Thermal Fault > 700 c | 3.560471976 | 0.4492677824 | 3.808988764 | Discharge of Low Energy, | High Energy Discharge | Thermal Fault >700 c | 0.4492677824 | 3.560471976 | 2.81024447 | 0.07373653687 | Arching | Arching | Arching | Arching
200 | D-6893 | 10 MVA | 33/6.6 KV | AREVA | 2006 | 8.1 | 125.874 | 15483.393 | 62494.74 | 95.985 | 1004.076 | 46.008 | 6.723 | 131.301 | 909.306 | 6.925354719 | 0.3655083655 | 19.53012048 | Arching | Arching,Low temprature thermal fault | Arching,Thermal Fault > 700 c | 6.925354719 | 0.3655083655 | 19.53012048 | Discharge of Low Energy, | High Energy Discharge | Thermal Fault >700 c | 0.3655083655 | 6.925354719 | 19.76408451 | 0.007393550686 | Arching | Arching | Arching | Arching
201 | 93ZG002/RH/01 | 25MVA | 33/6.9 | KIRLOSKAR | 1994 | 7.8 | 1.95 | 15432.144 | 60395.244 | 129.402 | 1204.71 | 3.042 | 2.34 | 8 | 5 | 0.625 | 1.56 | 3.418803419 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Arching,Thermal Fault > 700 c | 0.625 | 1.56 | 3.418803419 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.56 | 0.625 | 1.64365549 | 0.468 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
202 | 93ZG002/RH/03 | 25MVA | 33/6.9 | KIRLOSKAR | 1995 | 8.5 | 4.675 | 15901.46 | 65937.305 | 189.125 | 1781.26 | 5.355 | 9 | 5 | 7 | 1.4 | 1.145454545 | 0.5555555556 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 1.4 | 1.145454545 | 0.5555555556 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.145454545 | 1.4 | 1.307189542 | 1.285714286 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
203 | 93ZG002/RH/02 | 25MVA | 33/6.9 | KIRLOSKAR | 1995 | 8.5 | 5.865 | 16277.585 | 64988.11 | 206.465 | 2308.09 | 10.965 | 2.125 | 5.78 | 8 | 1.384083045 | 1.869565217 | 2.72 | Arching | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 1.384083045 | 1.869565217 | 2.72 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.869565217 | 1.384083045 | 0.7295941632 | 0.265625 | Thermal Decomposition, | Arching | Arching | Arching
204 | 9222/RV/453 | 25MVA | 33/6.9 | VOLTAMP | 1995 | 7.6 | 4.94 | 15187.004 | 57208.392 | 222.376 | 2773.696 | 7.22 | 5.168 | 8 | 9 | 1.125 | 1.461538462 | 1.547987616 | Arching | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 1.125 | 1.461538462 | 1.547987616 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.461538462 | 1.125 | 1.246537396 | 0.5742222222 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
205 | - | 25MVA | 33/6.9 | VOLTAMP | 1995 | 7.8 | 5.07 | 15828.072 | 58913.088 | 209.508 | 2646.15 | 4.134 | 2.574 | 8 | 3 | 0.375 | 0.8153846154 | 3.108003108 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Arching,Thermal Fault > 700 c | 0.375 | 0.8153846154 | 3.108003108 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.8153846154 | 0.375 | 0.7256894049 | 0.858 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
206 | 4740/1 | 25MVA | 33/6.9KV | BHARAT BIJLEE | 2003 | 8 | 4.64 | 15827.12 | 60442.64 | 225.76 | 2421.92 | 3.04 | 11 | 7 | 6 | 0.8571428571 | 0.6551724138 | 0.6363636364 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Partial discharge, Normal | 0.8571428571 | 0.6551724138 | 0.6363636364 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.6551724138 | 0.8571428571 | 1.973684211 | 1.833333333 | Arching | Arching | Arching | Thermal Decomposition,corona
207 | 4740/2 | 25MVA | 33/6.9KV | BHARAT BIJLEE | 2003 | 8 | 8.96 | 14761.76 | 62256.08 | 202.32 | 2043.92 | 3.2 | 6 | 9 | 8 | 0.8888888889 | 0.3571428571 | 1.5 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.8888888889 | 0.3571428571 | 1.5 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.3571428571 | 0.8888888889 | 2.5 | 0.75 | Arching | Arching | Arching | Thermal Decomposition,corona
208 | B-30654 | 275 MVA | (420/√3)/21 KV | ALSTOM | 2013 | 7.6 | 4.028 | 13402.22 | 61241.028 | 43.016 | 463.448 | 9 | 8 | 9 | 9 | 1 | 2.234359484 | 1.125 | Arching | Low temperature thermal | Low Temprature thermal Fault,Thermal Fault<700c | 1 | 2.234359484 | 1.125 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 2.234359484 | 1 | 1 | 0.8888888889 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
209 | B-30655 | 275 MVA | (420/√3)/21 KV | ALSTOM | 2013 | 7.9 | 4.819 | 15688.768 | 61898.949 | 48.901 | 644.245 | 1.185 | 9 | 8 | 5 | 0.625 | 0.2459016393 | 0.8888888889 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Partial discharge, Normal | 0.625 | 0.2459016393 | 0.8888888889 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.2459016393 | 0.625 | 4.219409283 | 1.8 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
210 | B-30656 | 275 MVA | (420/√3)/21 KV | ALSTOM | 2013 | 8.1 | 4.698 | 14130.6363 | 65215.0683 | 56.862 | 585.225 | 3.969 | 8 | 8 | 6 | 0.75 | 0.8448275862 | 1 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.75 | 0.8448275862 | 1 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.8448275862 | 0.75 | 1.511715797 | 1.333333333 | Arching | FALSE | Arching | Thermal Decomposition,corona
211 | B-30651 | 275 MVA | (420/√3)/11.5 KV | ALSTOM | 2012 | 8 | 4.08 | 15685.44 | 62607.44 | 102.64 | 1037.52 | 8.24 | 6 | 2.88 | 8 | 2.777777778 | 2.019607843 | 0.48 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 2.777777778 | 2.019607843 | 0.48 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 2.019607843 | 2.777777778 | 0.9708737864 | 0.75 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
212 | B-30657 | 275 MVA | (420/√3)/11.5 KV | ALSTOM | 2013 | 8.1 | 7.533 | 15342.048 | 63941.643 | 48.519 | 538.893 | 29.889 | 12 | 46.413 | 4 | 0.08618275052 | 3.967741935 | 3.86775 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Arching,Thermal Fault > 700 c | 0.08618275052 | 3.967741935 | 3.86775 | Thermal Fault> 300c and<700 c | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 3.967741935 | 0.08618275052 | 0.1338284988 | 3 | Thermal Decomposition, | Thermal Decomposition, | Thermal Decomposition,corona | Thermal Decomposition,corona
| B-30653 | 275 MVA | (420/√3)/11.5 KV | ALSTOM | 2012 | 8.5 | 4.335 | 16482.435 | 67215.025 | 55.675 | 642.515 | 4.76 | 11 | 7 | 55 | 7.857142857 | 1.098039216 | 0.6363636364 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 7.857142857 | 1.098039216 | 0.6363636364 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.098039216 | 7.857142857 | 11.55462185 | 0.2 | Thermal Decomposition, | Arching | Arching | Arching
214 | JN-22513 | 15 MVA | 132/6.9 KV | Voltamp | 2021 | 7.8 | 0.936 | 14949.012 | 61968.348 | 54.288 | 602.394 | 8 | 9 | 8 | 13 | 1.625 | 8.547008547 | 0.8888888889 | Arching | Low temperature thermal | Partial discharge, Normal | 1.625 | 8.547008547 | 0.8888888889 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 8.547008547 | 1.625 | 1.625 | 0.6923076923 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
215 | 18819 | 10 MVA | 33/6.6 KV | CP | 1964 | 8.5 | 1.955 | 18037.085 | 64912.205 | 117.725 | 1243.72 | 7.055 | 2.975 | 15.47 | 20 | 1.292824822 | 3.608695652 | 5.2 | Arching | Thermal Fault <700c, thermal fault >700c | Arching,Thermal Fault > 700 c | 1.292824822 | 3.608695652 | 5.2 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 3.608695652 | 1.292824822 | 2.834868887 | 0.14875 | Thermal Decomposition, | Arching | Arching | Arching
216 | B-26394 | 16/21 MVA | 11/6.6 | GEC | 1987 | 8 | 7.68 | 14623.52 | 63559.44 | 114 | 1170 | 2.96 | 8.24 | 19.28 | 32 | 1.659751037 | 0.3854166667 | 2.339805825 | Arching | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 1.659751037 | 0.3854166667 | 2.339805825 | Discharge of Low Energy, | High Energy Discharge | Thermal Fault >700 c | 0.3854166667 | 1.659751037 | 10.81081081 | 0.2575 | Arching | Arching | Arching | Arching
217 | 18450 | 10 MVA | 13.2/33 KV | - | - | 7.9 | 3.792 | 16985.79 | 59046.654 | 155.946 | 1644.938 | 12.482 | 1.896 | 13.509 | 15 | 1.110370864 | 3.291666667 | 7.125 | Arching | Thermal Fault <700c, thermal fault >700c | Arching,Thermal Fault > 700 c | 1.110370864 | 3.291666667 | 7.125 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 3.291666667 | 1.110370864 | 1.201730492 | 0.1264 | Thermal Decomposition, | Arching | Arching | Arching
218 | 17390 | 10 MVA | 13.2/33 KV | - | - | 8.5 | 64.175 | 15996.32 | 61937.63 | 190.57 | 2108.34 | 1237.345 | 319.345 | 2054.705 | 27.88 | 0.01356885782 | 19.2807947 | 6.43412297 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Arching,Thermal Fault > 700 c | 0.01356885782 | 19.2807947 | 6.43412297 | Thermal Fault> 300c and<700 c | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 19.2807947 | 0.01356885782 | 0.02253211513 | 11.45426829 | Thermal Decomposition, | Thermal Decomposition, | Thermal Decomposition,corona | Thermal Decomposition,corona
219 | 90118A 03 | 70 MVA | 220/6.9 KV | BHEL | 2013 | 8.3 | 4.565 | 15261.625 | 65929.141 | 94.205 | 832.573 | 1.494 | 9 | 5 | 5 | 1 | 0.3272727273 | 0.5555555556 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1 | 0.3272727273 | 0.5555555556 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.3272727273 | 1 | 3.346720214 | 1.8 | Arching | Arching | Arching | Thermal Decomposition,corona
220 | 90113A 04 | 70 MVA | 220/6.9 KV | BHEL | 2013 | 8.5 | 6.375 | 15902.48 | 67433.985 | 92.225 | 932.025 | 2.295 | 9 | 6 | 5 | 0.8333333333 | 0.36 | 0.6666666667 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Partial discharge, Normal | 0.8333333333 | 0.36 | 0.6666666667 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.36 | 0.8333333333 | 2.178649237 | 1.8 | Arching | Arching | Arching | Thermal Decomposition,corona
221 | T09548/4 | 80 MVA | 141.2/35.3 KV | CGL | 2010 | 8.8 | 5.984 | 18346.768 | 66785.136 | 119.328 | 1289.552 | 24.376 | 6.424 | 12.76 | 33 | 2.586206897 | 4.073529412 | 1.98630137 | Arching | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 2.586206897 | 4.073529412 | 1.98630137 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 4.073529412 | 2.586206897 | 1.353790614 | 0.1946666667 | Thermal Decomposition, | Arching | Arching | Arching
222 | T09548/4 | 80 MVA | 141.2/35.3 KV | CGL | 2010 | 8.1 | 7.857 | 16762.545 | 61758.288 | 126.765 | 1227.474 | 21.627 | 5.832 | 14.661 | 8 | 0.5456653707 | 2.75257732 | 2.513888889 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 0.5456653707 | 2.75257732 | 2.513888889 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 2.75257732 | 0.5456653707 | 0.3699079854 | 0.729 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
223 | 23953 | 10 MVA | 33/6.6 KV | CGL | 1971 | 8.7 | 3.393 | 16803.093 | 67145.817 | 161.124 | 1730.865 | 70.296 | 20.532 | 186.963 | 65 | 0.3476623717 | 20.71794872 | 9.105932203 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Arching,Thermal Fault > 700 c | 0.3476623717 | 20.71794872 | 9.105932203 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 20.71794872 | 0.3476623717 | 0.9246614317 | 0.3158769231 | Thermal Decomposition, | Thermal Decomposition, | Arching | Arching
224 | 23170 | 10 MVA | 33/6.6 KV | C Parksion | 1971 | 7.8 | 11.856 | 15400.008 | 60415.758 | 150.15 | 1468.038 | 4 | 11 | 8 | 56 | 7 | 0.3373819163 | 0.7272727273 | Arching | Low temperature thermal | Partial discharge, Normal | 7 | 0.3373819163 | 0.7272727273 | Discharge of Low Energy, | Discharge of Low Energy | thermal fault <300c | 0.3373819163 | 7 | 14 | 0.1964285714 | Arching | Arching | Arching | Arching
225 | MF-7158/01 | 15 MVA | 34.5/11 KV | CGL | 2008 | 8.5 | 4.335 | 17108.715 | 65618.725 | 122.57 | 1389.92 | 9.775 | 7 | 9 | 8 | 0.8888888889 | 2.254901961 | 1.285714286 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 0.8888888889 | 2.254901961 | 1.285714286 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 2.254901961 | 0.8888888889 | 0.8184143223 | 0.875 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
226 | AMN-002 | 25 MVA | 66/11 KV | ABB | 2017 | 7.9 | 12.008 | 15636.47 | 60790.658 | 158.079 | 1684.359 | 1.817 | 11 | 6 | 9 | 1.5 | 0.1513157895 | 0.5454545455 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1.5 | 0.1513157895 | 0.5454545455 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.1513157895 | 1.5 | 4.953219593 | 1.222222222 | Arching | Arching | Arching | Thermal Decomposition,corona
227 | APA-004 | 25 MVA | 66/11 KV | ABB | 2017 | 8.3 | 5.229 | 17101.237 | 62926.284 | 143.756 | 1657.427 | 5.229 | 18 | 8 | 7 | 0.875 | 1 | 0.4444444444 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Partial discharge, Normal | 0.875 | 1 | 0.4444444444 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 1 | 0.875 | 1.338688086 | 2.571428571 | Arching | Arching | Arching | Thermal Decomposition,corona
228 | JN-8121 | 25 MVA | 66/11 KV | VOLTAMP | 2003 | 8.1 | 4.536 | 15023.961 | 63619.02 | 147.906 | 1632.474 | 3.969 | 19 | 5 | 5 | 1 | 0.875 | 0.2631578947 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1 | 0.875 | 0.2631578947 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.875 | 1 | 1.259763165 | 3.8 | Arching | Arching | Arching | Thermal Decomposition,corona
229 | JN-8232/5 | 25 MVA | 66/11 KV | VOLTAMP | 2004 | 8.2 | 6.97 | 15914.56 | 62685.802 | 189.092 | 2021.956 | 8 | 4 | 7 | 9 | 1.285714286 | 1.147776184 | 1.75 | Arching | Low temperature thermal | Low Temprature thermal Fault,Thermal Fault<700c | 1.285714286 | 1.147776184 | 1.75 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.147776184 | 1.285714286 | 1.125 | 0.4444444444 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
230 | JN-5798/2 | 15 MVA | 66/11 KV | VOLTAMP | 2001 | 8.4 | 8.316 | 14533.596 | 66667.356 | 184.296 | 2006.088 | 9 | 8 | 8 | 9 | 1.125 | 1.082251082 | 1 | Arching | Low temperature thermal | Low Temprature thermal Fault,Thermal Fault<700c | 1.125 | 1.082251082 | 1 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.082251082 | 1.125 | 1 | 0.8888888889 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
231 | APA-002 | 25 MVA | 66/11 KV | ABB | 2017 | 8.1 | 10.773 | 14758.443 | 63536.319 | 185.976 | 1914.273 | 9 | 9 | 6 | 8 | 1.333333333 | 0.8354218881 | 0.6666666667 | Arching | Low temperature thermal | Partial discharge, Normal | 1.333333333 | 0.8354218881 | 0.6666666667 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.8354218881 | 1.333333333 | 0.8888888889 | 1.125 | Arching | Arching | Arching | Thermal Decomposition,corona
232 | APA-003 | 25 MVA | 66/11 KV | ABB | 2017 | 7.8 | 14.742 | 16041.246 | 59302.542 | 172.77 | 1818.336 | 6.63 | 6 | 5 | 5 | 1 | 0.4497354497 | 0.8333333333 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1 | 0.4497354497 | 0.8333333333 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.4497354497 | 1 | 0.754147813 | 1.2 | Arching | Arching | Arching | Thermal Decomposition,corona
233 | AMN-001 | 25 MVA | 66/11 KV | ABB | 2017 | 8.1 | 8.019 | 16098.102 | 61956.09 | 161.676 | 1671.435 | 5.589 | 5 | 9 | 9 | 1 | 0.696969697 | 1.8 | Arching | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 1 | 0.696969697 | 1.8 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.696969697 | 1 | 1.610305958 | 0.5555555556 | Arching | Arching | Arching | Thermal Decomposition,corona
234 | 224011492/10 | 25 MVA | 66/11 KV | SCHNEIDER | 2021 | 8.1 | 0.972 | 15006.384 | 63629.793 | 101.736 | 1074.303 | 9 | 9 | 6 | 7 | 1.166666667 | 9.259259259 | 0.6666666667 | Arching | Low temperature thermal | Partial discharge, Normal | 1.166666667 | 9.259259259 | 0.6666666667 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 9.259259259 | 1.166666667 | 0.7777777778 | 1.285714286 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
235 | 221100742/10 | 25 MVA | 66/11 KV | SCHNEIDER | 2019 | 7.9 | 9.559 | 15475.547 | 61182.024 | 146.545 | 1577.077 | 1.659 | 6 | 9 | 8 | 0.8888888889 | 0.173553719 | 1.5 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.8888888889 | 0.173553719 | 1.5 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.173553719 | 0.8888888889 | 4.822182037 | 0.75 | Arching | Arching | Arching | Thermal Decomposition,corona
236 | JN-8103/2 | 25 MVA | 66/11 KV | VOLTAMP | 2002 | 8.4 | 13.944 | 16058.196 | 65353.512 | 183.288 | 1933.764 | 13.692 | 9 | 10.164 | 9 | 0.8854781582 | 0.9819277108 | 1.129333333 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.8854781582 | 0.9819277108 | 1.129333333 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.9819277108 | 0.8854781582 | 0.657318142 | 1 | Arching | Arching | Arching | Thermal Decomposition,corona
237 | JN-5798/1 | 15 MVA | 66/11 KV | VOLTAMP | 2001 | 8.5 | 5.695 | 17330.055 | 65294.025 | 161.245 | 1699.405 | 6.715 | 7.99 | 13.855 | 8 | 0.5774088777 | 1.179104478 | 1.734042553 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 0.5774088777 | 1.179104478 | 1.734042553 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.179104478 | 0.5774088777 | 1.191362621 | 0.99875 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
238 | JN-2777 | 15 MVA | 66/11 KV | VOLTAMP | 1991 | 8.2 | 11.152 | 15756.792 | 63315.89 | 200.162 | 2133.886 | 13.366 | 9 | 9 | 9 | 1 | 1.198529412 | 1 | Arching | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 1 | 1.198529412 | 1 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.198529412 | 1 | 0.6733502918 | 1 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
239 | JN-3081 | 15 MVA | 66/11 KV | VOLTAMP | 1993 | 8.4 | 6.972 | 17104.92 | 64379.868 | 177.408 | 1849.764 | 5.292 | 12 | 8 | 7 | 0.875 | 0.7590361446 | 0.6666666667 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Partial discharge, Normal | 0.875 | 0.7590361446 | 0.6666666667 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.7590361446 | 0.875 | 1.322751323 | 1.714285714 | Arching | Arching | Arching | Thermal Decomposition,corona
240 | 10469 | 15 MVA | 66/11 KV | ETE | 1989 | 8.3 | 10.375 | 16388.682 | 63474.748 | 191.398 | 2038.729 | 5.229 | 8 | 7 | 6 | 0.8571428571 | 0.504 | 0.875 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Partial discharge, Normal | 0.8571428571 | 0.504 | 0.875 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.504 | 0.8571428571 | 1.147446931 | 1.333333333 | Arching | Arching | Arching | Thermal Decomposition,corona
241 | JN-3164/2 | 15 MVA | 66/11 KV | VOLTAMP | 1994 | 8.5 | 46.24 | 16210.86 | 65706.615 | 171.785 | 1804.72 | 8.16 | 1.785 | 13.09 | 20.995 | 1.603896104 | 0.1764705882 | 7.333333333 | Arching | Arching,Low temprature thermal fault | Arching,Thermal Fault > 700 c | 1.603896104 | 0.1764705882 | 7.333333333 | Discharge of Low Energy, | High Energy Discharge | Thermal Fault >700 c | 0.1764705882 | 1.603896104 | 2.572916667 | 0.08502024291 | Arching | Arching | Arching | Arching
242 | JN-3434 | 15 MVA | 66/11 KV | VOLTAMP | 1995 | 8.6 | 39.474 | 17659.326 | 65606.476 | 197.972 | 1974.818 | 6.794 | 9 | 12.04 | 4.816 | 0.4 | 0.1721132898 | 1.337777778 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.4 | 0.1721132898 | 1.337777778 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.1721132898 | 0.4 | 0.7088607595 | 1.868770764 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
243 | 222978419/10 | 25 MVA | 66/11 KV | SCHNEIDER | 2020 | 7.9 | 15.879 | 16507.05 | 60556.976 | 70.705 | 841.35 | 4.582 | 6 | 9 | 6 | 0.6666666667 | 0.2885572139 | 1.5 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.6666666667 | 0.2885572139 | 1.5 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.2885572139 | 0.6666666667 | 1.309471846 | 1 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
244 | JN-8171/1 | 25 MVA | 66/11 KV | VOLTAMP | 2003 | 8.3 | 3.984 | 16417.981 | 64042.551 | 177.205 | 1857.872 | 4.233 | 7 | 8 | 8 | 1 | 1.0625 | 1.142857143 | Arching | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 1 | 1.0625 | 1.142857143 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.0625 | 1 | 1.889912592 | 0.875 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
245 | JN-8171/2 | 25 MVA | 66/11 KV | VOLTAMP | 2003 | 8.1 | 6.885 | 16521.651 | 61294.239 | 187.272 | 1994.625 | 1.053 | 8 | 6 | 9 | 1.5 | 0.1529411765 | 0.75 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1.5 | 0.1529411765 | 0.75 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.1529411765 | 1.5 | 8.547008547 | 0.8888888889 | Arching | Arching | Arching | Thermal Decomposition,corona
246 | JN-8232/4 | 25 MVA | 66/11 KV | VOLTAMP | 2004 | 8.3 | 12.865 | 16657.602 | 63370.251 | 162.265 | 1745.905 | 7.968 | 9 | 3.735 | 8 | 2.141900937 | 0.6193548387 | 0.415 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 2.141900937 | 0.6193548387 | 0.415 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.6193548387 | 2.141900937 | 1.004016064 | 1.125 | Arching | Arching | Arching | Thermal Decomposition,corona
247 | JN-8232/8 | 25 MVA | 66/11 KV | VOLTAMP | 2004 | 8.2 | 12.71 | 16340.386 | 62360.918 | 192.782 | 2014.084 | 6.97 | 9 | 13.366 | 13 | 0.9726170881 | 0.5483870968 | 1.485111111 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.9726170881 | 0.5483870968 | 1.485111111 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.5483870968 | 0.9726170881 | 1.865136298 | 0.6923076923 | Arching | Arching | Arching | Thermal Decomposition,corona
248 | JN-8232/6 | 25 MVA | 66/11 KV | VOLTAMP | 2004 | 7.8 | 15.288 | 14908.998 | 60331.284 | 173.238 | 1819.35 | 7.722 | 11 | 5.85 | 4 | 0.6837606838 | 0.5051020408 | 0.5318181818 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Partial discharge, Normal | 0.6837606838 | 0.5051020408 | 0.5318181818 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.5051020408 | 0.6837606838 | 0.518000518 | 2.75 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
249 | JN-8232/7 | 25 MVA | 66/11 KV | VOLTAMP | 2004 | 8.3 | 18.343 | 17061.646 | 62557.266 | 182.766 | 1989.095 | 5.229 | 16 | 7 | 6 | 0.8571428571 | 0.2850678733 | 0.4375 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Partial discharge, Normal | 0.8571428571 | 0.2850678733 | 0.4375 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.2850678733 | 0.8571428571 | 1.147446931 | 2.666666667 | Arching | Arching | Arching | Thermal Decomposition,corona
250 | JN-8156/1 | 25 MVA | 66/11 KV | VOLTAMP | 2003 | 8.2 | 12.71 | 14862.09 | 65207.548 | 124.722 | 1368.17 | 5.084 | 11 | 7 | 9 | 1.285714286 | 0.4 | 0.6363636364 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1.285714286 | 0.4 | 0.6363636364 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.4 | 1.285714286 | 1.770259638 | 1.222222222 | Arching | Arching | Arching | Thermal Decomposition,corona
251 | JN-8156/2 | 25 MVA | 66/11 KV | VOLTAMP | 2003 | 8.3 | 8.964 | 15768.921 | 64994.229 | 134.626 | 1455.156 | 5.478 | 10 | 9 | 9 | 1 | 0.6111111111 | 0.9 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1 | 0.6111111111 | 0.9 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.6111111111 | 1 | 1.642935378 | 1.111111111 | Arching | Arching | Arching | Thermal Decomposition,corona
252 | AFQ-001 | 25 MVA | 66/11 KV | ABB | 2012 | 7.9 | 18.96 | 15941.726 | 60181.726 | 155.077 | 1703.398 | 13.035 | 2.607 | 16.116 | 10 | 0.6205013651 | 0.6875 | 6.181818182 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Arching,Thermal Fault > 700 c | 0.6205013651 | 0.6875 | 6.181818182 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.6875 | 0.6205013651 | 0.7671653241 | 0.2607 | Arching | Thermal Decomposition, | Arching | Arching
253 | JN-8103/3 | 25 MVA | 66/11 KV | VOLTAMP | 2002 | 8.2 | 51.578 | 17171.128 | 61503.444 | 216.152 | 2265.824 | 29.028 | 23.37 | 80.524 | 23.944 | 0.2973523422 | 0.5627980922 | 3.445614035 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Arching,Thermal Fault > 700 c | 0.2973523422 | 0.5627980922 | 3.445614035 | High Energy Discharges | High Energy Discharge | Thermal Fault >700 c | 0.5627980922 | 0.2973523422 | 0.8248587571 | 0.9760273973 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
254 | JN-8557/1 | 25 MVA | 66/11 KV | VOLTAMP | 2006 | 7.9 | 4.582 | 16498.992 | 60398.976 | 114.708 | 1047.224 | 0.948 | 10 | 9 | 9 | 1 | 0.2068965517 | 0.9 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1 | 0.2068965517 | 0.9 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.2068965517 | 1 | 9.493670886 | 1.111111111 | Arching | Arching | Arching | Thermal Decomposition,corona
255 | JN-8076 | 15 MVA | 66/11 KV | VOLTAMP | 2002 | 8 | 7.68 | 16749.84 | 60094.64 | 180.48 | 1857.12 | 4.48 | 11 | 7 | 6 | 0.8571428571 | 0.5833333333 | 0.6363636364 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Partial discharge, Normal | 0.8571428571 | 0.5833333333 | 0.6363636364 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.5833333333 | 0.8571428571 | 1.339285714 | 1.833333333 | Arching | Arching | Arching | Thermal Decomposition,corona
256 | JN-5598 | 25 MVA | 66/11 KV | VOLTAMP | 2000 | 8.6 | 69.144 | 17299.846 | 65496.052 | 189.974 | 2002.768 | 68.112 | 17.372 | 139.664 | 134 | 0.9594455264 | 0.9850746269 | 8.03960396 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Arching,Thermal Fault > 700 c | 0.9594455264 | 0.9850746269 | 8.03960396 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.9850746269 | 0.9594455264 | 1.967347898 | 0.129641791 | Arching | Arching | Arching | Arching
257 | JN-8103/1 | 25 MVA | 66/11 KV | VOLTAMP | 2002 | 7.9 | 7.821 | 16564.562 | 59375.926 | 171.114 | 1861.556 | 1.817 | 12 | 7 | 4 | 0.5714285714 | 0.2323232323 | 0.5833333333 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Partial discharge, Normal | 0.5714285714 | 0.2323232323 | 0.5833333333 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.2323232323 | 0.5714285714 | 2.20143093 | 3 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
258 | APA-001 | 25 MVA | 66/11 KV | ABB | 2017 | 8.2 | 9.922 | 16286.676 | 63258.162 | 143.828 | 1555.458 | 7 | 16 | 9 | 5 | 0.5555555556 | 0.7055029228 | 0.5625 | Partial discharge,Low Temprature thermal fault, | Low temperature thermal | Partial discharge, Normal | 0.5555555556 | 0.7055029228 | 0.5625 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.7055029228 | 0.5555555556 | 0.7142857143 | 3.2 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
259 | ABP-01 | 40 MVA | 66/11 KV | ABB | 2018 | 8.2 | 7.298 | 16580.564 | 63504.49 | 116.522 | 1281.824 | 3.69 | 9 | 7 | 7 | 1 | 0.5056179775 | 0.7777777778 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1 | 0.5056179775 | 0.7777777778 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.5056179775 | 1 | 1.89701897 | 1.285714286 | Arching | Arching | Arching | Thermal Decomposition,corona
260 | ABP-02 | 40 MVA | 66/11 KV | ABB | 2018 | 7.9 | 7.584 | 15543.882 | 61315.455 | 135.959 | 1447.675 | 5.451 | 7 | 9 | 9 | 1 | 0.71875 | 1.285714286 | Arching | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 1 | 0.71875 | 1.285714286 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.71875 | 1 | 1.651073198 | 0.7777777778 | Arching | Arching | Arching | Thermal Decomposition,corona
261 | JN-8232/1 | 25 MVA | 66/11 KV | VOLTAMP | 2004 | 8.4 | 9.24 | 16947.84 | 64113.084 | 156.492 | 1676.892 | 3.276 | 6 | 5 | 8 | 1.6 | 0.3545454545 | 0.8333333333 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1.6 | 0.3545454545 | 0.8333333333 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.3545454545 | 1.6 | 2.442002442 | 0.75 | Arching | Arching | Arching | Thermal Decomposition,corona
262 | JN-8232/2 | 25 MVA | 66/11 KV | VOLTAMP | 2004 | 8.3 | 13.529 | 16746.08 | 63331.075 | 170.565 | 1760.762 | 5.063 | 4 | 9 | 7 | 0.7777777778 | 0.3742331288 | 2.25 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.7777777778 | 0.3742331288 | 2.25 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.3742331288 | 0.7777777778 | 1.382579498 | 0.5714285714 | Arching | Arching | Arching | Thermal Decomposition,corona
263 | JN-8192/1 | 25 MVA | 66/11 KV | VOLTAMP | 2004 | 8.3 | 6.474 | 16746.08 | 63546.792 | 185.256 | 1961.456 | 9.213 | 5.727 | 21.082 | 23 | 1.090978086 | 1.423076923 | 3.68115942 | Arching | Thermal Fault <700c, thermal fault >700c | Arching,Thermal Fault > 700 c | 1.090978086 | 1.423076923 | 3.68115942 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.423076923 | 1.090978086 | 2.496472376 | 0.249 | Thermal Decomposition, | Arching | Arching | Arching
264 | JN-8192/2 | 25 MVA | 66/11 KV | VOLTAMP | 2004 | 7.9 | 8.295 | 15939.04 | 60217.908 | 162.977 | 1706.084 | 4.424 | 8 | 7 | 3 | 0.4285714286 | 0.5333333333 | 0.875 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Partial discharge, Normal | 0.4285714286 | 0.5333333333 | 0.875 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.5333333333 | 0.4285714286 | 0.678119349 | 2.666666667 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
265 | JN-5662 | 25 MVA | 66/11 KV | VOLTAMP | 2001 | 8.3 | 7.968 | 16746.08 | 63203.006 | 192.892 | 2039.144 | 5.229 | 9 | 8 | 21 | 2.625 | 0.65625 | 0.8888888889 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 2.625 | 0.65625 | 0.8888888889 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.65625 | 2.625 | 4.016064257 | 0.4285714286 | Arching | Arching | Arching | Thermal Decomposition,corona
266 | JN-8103/4 | 25 MVA | 66/11 KV | VOLTAMP | 2002 | 8 | 34.56 | 16140.8 | 60918.56 | 184.16 | 1916.16 | 14.72 | 5 | 53.12 | 23.68 | 0.4457831325 | 0.4259259259 | 10.624 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Arching,Thermal Fault > 700 c | 0.4457831325 | 0.4259259259 | 10.624 | High Energy Discharges | High Energy Discharge | Thermal Fault >700 c | 0.4259259259 | 0.4457831325 | 1.608695652 | 0.2111486486 | Arching | Thermal Decomposition, | Arching | Arching
267 | JN-8232/3 | 25 MVA | 66/11 KV | VOLTAMP | 2004 | 8.1 | 8.019 | 16342.56 | 61680.042 | 178.281 | 1800.711 | 5.103 | 10 | 9 | 3 | 0.3333333333 | 0.6363636364 | 0.9 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Partial discharge, Normal | 0.3333333333 | 0.6363636364 | 0.9 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.6363636364 | 0.3333333333 | 0.5878894768 | 3.333333333 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
268 | B-30087 | 24 MVA | 33/0.385 KV | AREVA | 2007 | 8.1 | 1.539 | 15838.092 | 62699.589 | 110.565 | 1232.334 | 8.586 | 11 | 7 | 4 | 0.5714285714 | 5.578947368 | 0.6363636364 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 0.5714285714 | 5.578947368 | 0.6363636364 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 5.578947368 | 0.5714285714 | 0.4658746797 | 2.75 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
269 | B-29914 | 24 MVA | 33/0.385 KV | ALSTOM | 2005 | 7.5 | 3.9 | 14896.95 | 57686.775 | 106.875 | 1264.2 | 6.975 | 12 | 6 | 3 | 0.5 | 1.788461538 | 0.5 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 0.5 | 1.788461538 | 0.5 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.788461538 | 0.5 | 0.4301075269 | 4 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
270 | 17391 | 10 MVA | 132/33 KV | -- | -- | 8.4 | 62.076 | 16249.632 | 61178.964 | 186.06 | 2205.42 | 1298.976 | 295.092 | 2019.864 | 26.208 | 0.012975131 | 20.9255751 | 6.844861941 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Arching,Thermal Fault > 700 c | 0.012975131 | 20.9255751 | 6.844861941 | Thermal Fault> 300c and<700 c | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 20.9255751 | 0.012975131 | 0.0201758924 | 11.25961538 | Thermal Decomposition, | Thermal Decomposition, | Thermal Decomposition,corona | Thermal Decomposition,corona
271 | 173717/1 | 10 MVA | - | - | - | 7.8 | 6.318 | 15846.012 | 59167.914 | 194.142 | 2067.936 | 8.034 | 9 | 10.764 | 11 | 1.021924935 | 1.271604938 | 1.196 | Arching | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 1.021924935 | 1.271604938 | 1.196 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.271604938 | 1.021924935 | 1.369180981 | 0.8181818182 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
272 | 120383-2 | 25 MVA | 22/11 KV | TELK | 1997 | 7.6 | 3.952 | 15042.68 | 58482.152 | 136.192 | 1357.588 | 5.7 | 6 | 1.9 | 23 | 12.10526316 | 1.442307692 | 0.3166666667 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 12.10526316 | 1.442307692 | 0.3166666667 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.442307692 | 12.10526316 | 4.035087719 | 0.2608695652 | Thermal Decomposition, | Arching | Arching | Arching
273 | 120383-2 | 25 MVA | 22/11 KV | TELK | 1997 | 7.9 | 4.819 | 16277.081 | 60683.692 | 141.805 | 1472.165 | 6.478 | 4 | 1.817 | 10 | 5.503577325 | 1.344262295 | 0.45425 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 5.503577325 | 1.344262295 | 0.45425 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.344262295 | 5.503577325 | 1.543686323 | 0.4 | Thermal Decomposition, | Arching | Arching | Arching
274 | 120383-1 | 25 MVA | 22/11 KV | TELK | 1997 | 8.4 | 5.46 | 15580.404 | 65975.28 | 117.18 | 1255.968 | 4.704 | 7 | 9 | 7 | 0.7777777778 | 0.8615384615 | 1.285714286 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.7777777778 | 0.8615384615 | 1.285714286 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.8615384615 | 0.7777777778 | 1.488095238 | 1 | Arching | Arching | Arching | Thermal Decomposition,corona
275 | 120383-1 | 25 MVA | 22/11 KV | TELK | 1997 | 8.4 | 3.696 | 15264.816 | 66123.204 | 113.82 | 1261.848 | 6.804 | 9 | 8 | 5 | 0.625 | 1.840909091 | 0.8888888889 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 0.625 | 1.840909091 | 0.8888888889 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.840909091 | 0.625 | 0.734861846 | 1.8 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
276 | 3166/1 | 26.5 MVA | 33/6.9 KV | VOLTAMP | 1994 | 7.8 | 4.368 | 15713.178 | 59773.35 | 129.168 | 1371.786 | 15.834 | 9.282 | 23.244 | 3 | 0.1290655653 | 3.625 | 2.504201681 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 0.1290655653 | 3.625 | 2.504201681 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 3.625 | 0.1290655653 | 0.1894657067 | 3.094 | Thermal Decomposition, | Thermal Decomposition, | Thermal Decomposition,corona | Thermal Decomposition,corona
277 | 3366/2 | 26.5 MVA | 33/6.9 KV | VOLTAMP | 1994 | 7.8 | 35.49 | 15636.504 | 59463.924 | 184.47 | 1912.95 | 66.612 | 174.408 | 10.608 | 22 | 2.073906486 | 1.876923077 | 0.06082289803 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 2.073906486 | 1.876923077 | 0.06082289803 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | Partial Discharges, | 1.876923077 | 2.073906486 | 0.3302708221 | 7.927636364 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
278 | 3166/3 | 26.5 MVA | 33/6.9 KV | VOLTAMP | 1994 | 8.2 | 7.298 | 16124.07 | 62488.592 | 217.956 | 2306.168 | 6.97 | 9 | 9 | 8 | 0.8888888889 | 0.9550561798 | 1 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.8888888889 | 0.9550561798 | 1 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.9550561798 | 0.8888888889 | 1.147776184 | 1.125 | Arching | Arching | Arching | Thermal Decomposition,corona
279 | JN-4206/1 | 26.5 MVA | 33/6.9 KV | VOLTAMP | 1997 | 8.1 | 6.885 | 14634.189 | 63905.436 | 190.431 | 1623.321 | 22.842 | 5.346 | 1.863 | 5 | 2.683843264 | 3.317647059 | 0.3484848485 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 2.683843264 | 3.317647059 | 0.3484848485 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 3.317647059 | 2.683843264 | 0.2188950179 | 1.0692 | Thermal Decomposition, | Arching | Thermal Decomposition,corona | Thermal Decomposition,corona
280 | JN-4206/3 | 26.5 MVA | 33/6.9 KV | VOLTAMP | 1997 | 8.4 | 9.324 | 15929.34 | 65229.192 | 165.06 | 1794.072 | 8.568 | 10 | 1.932 | 9 | 4.658385093 | 0.9189189189 | 0.1932 | Arching | Low temperature thermal | Partial discharge, Normal | 4.658385093 | 0.9189189189 | 0.1932 | Discharge of Low Energy, | High Energy Discharge | Partial Discharges, | 0.9189189189 | 4.658385093 | 1.050420168 | 1.111111111 | Arching | Arching | Arching | Thermal Decomposition,corona
281 | JN-4206/2 | 26.5 MVA | 33/6.9 KV | VOLTAMP | 1997 | 8.2 | 8.118 | 16517.752 | 62617.25 | 180.564 | 1938.07 | 19.106 | 6.232 | 8.036 | 4 | 0.4977600796 | 2.353535354 | 1.289473684 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 0.4977600796 | 2.353535354 | 1.289473684 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 2.353535354 | 0.4977600796 | 0.2093583168 | 1.558 | Thermal Decomposition, | Thermal Decomposition, | Thermal Decomposition,corona | Thermal Decomposition,corona
282 | 5019/2 | 40 MVA | 33/11.5 KV | BBL | 2007 | 7.9 | 4.977 | 15060.165 | 60478.055 | 220.015 | 2264.377 | 5.609 | 6.715 | 8 | 6 | 0.75 | 1.126984127 | 1.191362621 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 0.75 | 1.126984127 | 1.191362621 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.126984127 | 0.75 | 1.069709396 | 1.119166667 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
283 | 5019/1 | 40 MVA | 33/11.5 KV | BBL | 2007 | 8.2 | 4.264 | 16143.668 | 62772.886 | 191.47 | 1683.952 | 4.264 | 9 | 6 | 8 | 1.333333333 | 1 | 0.6666666667 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1.333333333 | 1 | 0.6666666667 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 1 | 1.333333333 | 1.876172608 | 1.125 | Arching | Arching | Arching | Thermal Decomposition,corona
284 | 3166/4 | 26.5 MVA | 33/6.9 KV | VOLTAMP | 1994 | 7.9 | 4.424 | 15038.124 | 61347.687 | 121.344 | 1308.714 | 3.318 | 6 | 9 | 6 | 0.6666666667 | 0.75 | 1.5 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.6666666667 | 0.75 | 1.5 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.75 | 0.6666666667 | 1.808318264 | 1 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
285 | 200949/8 | 50 MVA | 11/34.5 KV | BHEL | 1995 | 8.1 | 6.966 | 15031.089 | 63692.325 | 115.425 | 1298.025 | 1.863 | 10 | 5 | 9 | 1.8 | 0.2674418605 | 0.5 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1.8 | 0.2674418605 | 0.5 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.2674418605 | 1.8 | 4.830917874 | 1.111111111 | Arching | Arching | Arching | Thermal Decomposition,corona
286 | 200949/9 | 50 MVA | 11/34.5 KV | BHEL | 1995 | 8.3 | 10.043 | 16297.714 | 64825.075 | 102.505 | 1136.187 | 21.248 | 7.968 | 12.948 | 5 | 0.3861600247 | 2.115702479 | 1.625 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 0.3861600247 | 2.115702479 | 1.625 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 2.115702479 | 0.3861600247 | 0.2353162651 | 1.5936 | Thermal Decomposition, | Thermal Decomposition, | Thermal Decomposition,corona | Thermal Decomposition,corona
287 | TBI-623000451/2 | 16 MVA | 33/6.9 KV | SCHEINDER | 2012 | 7.6 | 8.436 | 14872.668 | 58148.892 | 177.308 | 2062.792 | 44.688 | 8.284 | 30.856 | 8 | 0.2592688618 | 5.297297297 | 3.724770642 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Arching,Thermal Fault > 700 c | 0.2592688618 | 5.297297297 | 3.724770642 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 5.297297297 | 0.2592688618 | 0.179018976 | 1.0355 | Thermal Decomposition, | Thermal Decomposition, | Thermal Decomposition,corona | Thermal Decomposition,corona
288 | TBI-623000451/1 | 16 MVA | 33/6.9 KV | SCHEINDER | 2012 | 7.9 | 6.952 | 15915.577 | 60307.731 | 171.825 | 1750.324 | 5.451 | 9 | 9 | 9 | 1 | 0.7840909091 | 1 | Arching | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 1 | 0.7840909091 | 1 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.7840909091 | 1 | 1.651073198 | 1 | Arching | Arching | Arching | Thermal Decomposition,corona
289 | 5391/1 | 24 MVA | 11/34.5 KV | BBL | 2014 | 8.2 | 10.496 | 16014.764 | 62778.298 | 185.566 | 1940.53 | 16.564 | 5.576 | 4.592 | 6 | 1.306620209 | 1.578125 | 0.8235294118 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 1.306620209 | 1.578125 | 0.8235294118 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.578125 | 1.306620209 | 0.3622313451 | 0.9293333333 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
290 | 6007245 | 285 MVA | 21/420/√3 KV | BHEL | 2016 | 7.9 | 1.817 | 15162.786 | 62022.189 | 60.514 | 625.285 | 2.528 | 9 | 1.215 | 8 | 6.58436214 | 1.391304348 | 0.135 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 6.58436214 | 1.391304348 | 0.135 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | Partial Discharges, | 1.391304348 | 6.58436214 | 3.164556962 | 1.125 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
291 | 6007246 | 285 MVA | 21/420/√3 KV | BHEL | 2016 | 8.1 | 1.944 | 16388.325 | 63074.214 | 72.576 | 746.334 | 1.215 | 7 | 2.805 | 4 | 1.426024955 | 0.625 | 0.4007142857 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1.426024955 | 0.625 | 0.4007142857 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.625 | 1.426024955 | 3.29218107 | 1.75 | Arching | Arching | Arching | Thermal Decomposition,corona
292 | 6007247 | 285 MVA | 21/420/√3 KV | BHEL | 2016 | 8.5 | 3.655 | 15545.99 | 67562.675 | 69.275 | 736.525 | 2.805 | 8 | 6.96 | 7 | 1.005747126 | 0.7674418605 | 0.87 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1.005747126 | 0.7674418605 | 0.87 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.7674418605 | 1.005747126 | 2.495543672 | 1.142857143 | Arching | Arching | Arching | Thermal Decomposition,corona
293 | 90118B06 | 70 MVA | 21/6.9 KV | TOSHIBA | 2015 | 8 | 8.4 | 15211.2 | 63358.56 | 108.4 | 641.76 | 6.96 | 9 | 9.047 | 4 | 0.4421355145 | 0.8285714286 | 1.005222222 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.4421355145 | 0.8285714286 | 1.005222222 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.8285714286 | 0.4421355145 | 0.5747126437 | 2.25 | FALSE | Thermal Decomposition, | Arching | Thermal Decomposition,corona
294 | 90118B03 | 70 MVA | 21/6.9 KV | TOSHIBA | 2015 | 8.3 | 6.806 | 16830.574 | 64411.984 | 126.243 | 1120.168 | 9.047 | 6 | 12.956 | 8 | 0.6174745292 | 1.329268293 | 2.159333333 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 0.6174745292 | 1.329268293 | 2.159333333 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.329268293 | 0.6174745292 | 0.8842710291 | 0.75 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
295 | 66189 | 28 MVA | 33/0.310 KV | -- | 2010 | 8.2 | 6.97 | 14996.488 | 64269.55 | 135.628 | 1440.248 | 12.956 | 9 | 1.68 | 5 | 2.976190476 | 1.858823529 | 0.1866666667 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 2.976190476 | 1.858823529 | 0.1866666667 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | Partial Discharges, | 1.858823529 | 2.976190476 | 0.3859215807 | 1.8 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
296 | 66190 | 28 MVA | 33/0.310 KV | -- | 2010 | 8 | 4.16 | 15725.2 | 62032.16 | 113.84 | 1250.56 | 1.68 | 6 | 6.08 | 9 | 1.480263158 | 0.4038461538 | 1.013333333 | Arching | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 1.480263158 | 0.4038461538 | 1.013333333 | Discharge of Low Energy, | High Energy Discharge | Thermal Fault >700 c | 0.4038461538 | 1.480263158 | 5.357142857 | 0.6666666667 | Arching | Arching | Arching | Thermal Decomposition,corona
297 | -- | 80 MVA | 132/33 KV | TELK | 2003 | 8 | 7.04 | 15708.32 | 62110.8 | 132.64 | 1351.76 | 6.08 | 9 | 19.352 | 4 | 0.2066969822 | 0.8636363636 | 2.150222222 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.2066969822 | 0.8636363636 | 2.150222222 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.8636363636 | 0.2066969822 | 0.6578947368 | 2.25 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
298 | -- | 80 MVA | 132/33 KV | TELK | 1999 | 8.2 | 10.168 | 16519.474 | 61516.236 | 257.89 | 2670.166 | 19.352 | 6 | 11.398 | 7 | 0.6141428321 | 1.903225806 | 1.899666667 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 0.6141428321 | 1.903225806 | 1.899666667 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.903225806 | 0.6141428321 | 0.3617197189 | 0.8571428571 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
299 | LEL 110667 | 13 MVA | 33/3.3 KV | Siemens | 2012 | 8.1 | 1.863 | 16253.298 | 62800.677 | 92.016 | 1054.134 | 3.159 | 9 | 8 | 99 | 12.375 | 1.695652174 | 0.8888888889 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 12.375 | 1.695652174 | 0.8888888889 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.695652174 | 12.375 | 31.33903134 | 0.09090909091 | Thermal Decomposition, | Arching | Arching | Arching
300 | B-29288 | 10 MVA | 13..2/3.45 KV | ALSTOM | 1996 | 8.5 | 15.81 | 17124.78 | 63627.94 | 252.28 | 2654.89 | 27.71 | 7.565 | 35.53 | 45 | 1.266535322 | 1.752688172 | 4.696629213 | Arching | Thermal Fault <700c, thermal fault >700c | Arching,Thermal Fault > 700 c | 1.266535322 | 1.752688172 | 4.696629213 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.752688172 | 1.266535322 | 1.623962468 | 0.1681111111 | Thermal Decomposition, | Arching | Arching | Arching
301 | -- | 80 MVA | 141.2/35.3 KV | ABB | 2008 | 8.2 | 2.05 | 16118.084 | 64153.192 | 101.762 | 932.996 | 9 | 2.805 | 7 | 224 | 32 | 4.390243902 | 2.495543672 | Arching | Low temperature thermal | Low Temprature thermal Fault,Thermal Fault<700c | 32 | 4.390243902 | 2.495543672 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 4.390243902 | 32 | 24.88888889 | 0.01252232143 | Thermal Decomposition, | Arching | Arching | Arching
302 | -- | 10 MVA | 33/6.6 KV | CP | 1971 | 8.1 | 4.536 | 15436.008 | 62845.065 | 142.155 | 1536.165 | 2.916 | 6.96 | 8 | 55 | 6.875 | 0.6428571429 | 1.149425287 | Arching | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 6.875 | 0.6428571429 | 1.149425287 | Discharge of Low Energy, | High Energy Discharge | Thermal Fault >700 c | 0.6428571429 | 6.875 | 18.86145405 | 0.1265454545 | Arching | Arching | Arching | Arching
303 | -- | 15 MVA | 33/6.6 KV | Alstom | 2006 | 8.4 | 1.932 | 16811.13 | 64289.232 | 159.432 | 1600.704 | 9 | 9.047 | 9 | 8 | 0.8888888889 | 4.658385093 | 0.9948049077 | Partial discharge,Low Temprature thermal fault, | Low temperature thermal | Partial discharge, Normal | 0.8888888889 | 4.658385093 | 0.9948049077 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 4.658385093 | 0.8888888889 | 0.8888888889 | 1.130875 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
304 | -- | 80 MVA | 132/34.5 KV | CGL | 2003 | 8.2 | 2.87 | 14897.186 | 64886.026 | 101.27 | 1120.858 | 7.954 | 12.956 | 8 | 45 | 5.625 | 2.771428571 | 0.6174745292 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 5.625 | 2.771428571 | 0.6174745292 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 2.771428571 | 5.625 | 5.657530802 | 0.2879111111 | Thermal Decomposition, | Arching | Arching | Arching
305 | D 11042 | 15 MVA | 33/6.6 KV | SCHNEIDER | 2012 | 7.7 | 14.245 | 15381.905 | 59471.874 | 102.025 | 1120.812 | 4.312 | 1.68 | 9 | 8 | 0.8888888889 | 0.3027027027 | 5.357142857 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Arching,Thermal Fault > 700 c | 0.8888888889 | 0.3027027027 | 5.357142857 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.3027027027 | 0.8888888889 | 1.85528757 | 0.21 | Arching | Arching | Arching | Arching
306 | D 11042 | 15 MVA | 33/6.6 KV | SCHNEIDER | 2012 | 8.1 | 11.826 | 16838.766 | 61545.987 | 172.692 | 1784.511 | 10.125 | 6.08 | 8 | 9 | 1.125 | 0.8561643836 | 1.315789474 | Arching | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 1.125 | 0.8561643836 | 1.315789474 | Discharge of Low Energy, | High Energy Discharge | Thermal Fault >700 c | 0.8561643836 | 1.125 | 0.8888888889 | 0.6755555556 | Arching | Arching | Arching | Thermal Decomposition,corona
307 | D 11043 | 15 MVA | 33/6.6 KV | SCHNEIDER | 2012 | 7.9 | 8.058 | 16166.323 | 60722.639 | 120.159 | 1334.784 | 5.372 | 5 | 7 | 5 | 0.7142857143 | 0.6666666667 | 1.4 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.7142857143 | 0.6666666667 | 1.4 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.6666666667 | 0.7142857143 | 0.9307520477 | 1 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
308 | D 11043 | 15 MVA | 33/6.6 KV | SCHNEIDER | 2012 | 8.2 | 16.318 | 16310.702 | 62119.51 | 215.742 | 2287.472 | 10.824 | 11.398 | 18.942 | 18 | 0.950269243 | 0.6633165829 | 1.661870504 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.950269243 | 0.6633165829 | 1.661870504 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.6633165829 | 0.950269243 | 1.662971175 | 0.6332222222 | Arching | Arching | Arching | Thermal Decomposition,corona
309 | MT-7440/01 | 15 MVA | 33/6.6 KV | CGL | 2011 | 7.9 | 6.794 | 15845.425 | 60160.475 | 183.675 | 1868.666 | 6.004 | 9 | 7.584 | 7 | 0.9229957806 | 0.8837209302 | 0.8426666667 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Partial discharge, Normal | 0.9229957806 | 0.8837209302 | 0.8426666667 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.8837209302 | 0.9229957806 | 1.165889407 | 1.285714286 | Arching | Arching | Arching | Thermal Decomposition,corona
310 | MT-7440/01 | 15 MVA | 33/6.6 KV | CGL | 2011 | 8.4 | 3.024 | 17283.42 | 64249.668 | 126.168 | 1334.676 | 3.864 | 8 | 7.14 | 7 | 0.9803921569 | 1.277777778 | 0.8925 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 0.9803921569 | 1.277777778 | 0.8925 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.277777778 | 0.9803921569 | 1.811594203 | 1.142857143 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
311 | D 11044 | 15 MVA | 33/6.6 KV | SCHNEIDER | 2012 | 8.4 | 8.064 | 17142.3 | 64570.38 | 94.332 | 1037.904 | 7.14 | 8 | 1.932 | 7 | 3.623188406 | 0.8854166667 | 0.2415 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 3.623188406 | 0.8854166667 | 0.2415 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.8854166667 | 3.623188406 | 0.9803921569 | 1.142857143 | Arching | Arching | Arching | Thermal Decomposition,corona
312 | D 11044 | 15 MVA | 33/6.6 KV | SCHNEIDER | 2012 | 8.3 | 18.675 | 17516.652 | 62295.318 | 196.295 | 2063.795 | 5.229 | 2.49 | 6 | 8 | 1.333333333 | 0.28 | 2.409638554 | Arching | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 1.333333333 | 0.28 | 2.409638554 | Discharge of Low Energy, | High Energy Discharge | Thermal Fault >700 c | 0.28 | 1.333333333 | 1.529929241 | 0.31125 | Arching | Arching | Arching | Arching
313 | MT-7440/02 | 15 MVA | 33/6.6 KV | CGL | 2011 | 8.1 | 12.636 | 16761.573 | 61533.513 | 125.145 | 1368.009 | 4.536 | 9 | 8 | 5 | 0.625 | 0.358974359 | 0.8888888889 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Partial discharge, Normal | 0.625 | 0.358974359 | 0.8888888889 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.358974359 | 0.625 | 1.102292769 | 1.8 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
314 | MT-7440/02 | 15 MVA | 33/6.6 KV | CGL | 2011 | 8.3 | 7.055 | 16852.652 | 63844.762 | 157.285 | 1657.344 | 5.644 | 7 | 5 | 9 | 1.8 | 0.8 | 0.7142857143 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1.8 | 0.8 | 0.7142857143 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.8 | 1.8 | 1.594613749 | 0.7777777778 | Arching | Arching | Arching | Thermal Decomposition,corona
315 | MT-5296/1 | 15 MVA | 33/6.6 KV | CGL | 2005 | 8.1 | 5.103 | 16379.577 | 62425.161 | 115.101 | 1244.322 | 5.265 | 6 | 6 | 7 | 1.166666667 | 1.031746032 | 1 | Arching | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 1.166666667 | 1.031746032 | 1 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.031746032 | 1.166666667 | 1.329534663 | 0.8571428571 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
316 | 7339824/1 | 16 MVA | 33/6.6 KV | SCHNEIDER | 2017 | 7.6 | 5.244 | 14309.812 | 60073.06 | 91.352 | 1053.056 | 2.736 | 10 | 8 | 4 | 0.5 | 0.5217391304 | 0.8 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Partial discharge, Normal | 0.5 | 0.5217391304 | 0.8 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.5217391304 | 0.5 | 1.461988304 | 2.5 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
317 | 220875172/01 | 16 MVA | 33/6.6 KV | SCHNEIDER | 2018 | 7.8 | 16.692 | 15681.978 | 60270.21 | 106.782 | 1179.594 | 7.488 | 11 | 4.056 | 3 | 0.7396449704 | 0.4485981308 | 0.3687272727 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Partial discharge, Normal | 0.7396449704 | 0.4485981308 | 0.3687272727 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.4485981308 | 0.7396449704 | 0.4006410256 | 3.666666667 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
318 | 38431 | 10 MVA | 33/6.6 KV | HACK BRIDGE | 1989 | 8.1 | 5.751 | 15356.142 | 63576.657 | 129.762 | 1406.565 | 7.209 | 9 | 5.103 | 8 | 1.567705271 | 1.253521127 | 0.567 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 1.567705271 | 1.253521127 | 0.567 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.253521127 | 1.567705271 | 1.109723956 | 1.125 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
319 | 4163/1 | 10 MVA | 33/6.6 KV | BBL | 1996 | 8.4 | 33.264 | 13310.304 | 67392.024 | 218.652 | 2284.464 | 20.748 | 7.476 | 29.904 | 34 | 1.136971643 | 0.6237373737 | 4 | Arching | Arching,Low temprature thermal fault | Arching,Thermal Fault > 700 c | 1.136971643 | 0.6237373737 | 4 | Discharge of Low Energy, | High Energy Discharge | Thermal Fault >700 c | 0.6237373737 | 1.136971643 | 1.638712165 | 0.2198823529 | Arching | Arching | Arching | Arching
320 | 4940/1 | 15 MVA | 33/6.6 KV | BBL | 2006 | 8.1 | 13.122 | 15160.851 | 62896.581 | 194.724 | 2067.363 | 8 | 8 | 5 | 8 | 1.6 | 0.6096631611 | 0.625 | Arching | Low temperature thermal | Partial discharge, Normal | 1.6 | 0.6096631611 | 0.625 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.6096631611 | 1.6 | 1 | 1 | Arching | Arching | Arching | Thermal Decomposition,corona
321 | JN.21071 | 10 MVA | 132KV/6.9KV | VOLTAMP | 2008 | 8.3 | 2.905 | 16016.344 | 63385.191 | 246.178 | 2563.455 | 2.656 | 9 | 7 | 9 | 1.285714286 | 0.9142857143 | 0.7777777778 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1.285714286 | 0.9142857143 | 0.7777777778 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.9142857143 | 1.285714286 | 3.388554217 | 1 | Arching | Arching | Arching | Thermal Decomposition,corona
322 | JN.21071 | 10 MVA | 132KV/6.9KV | VOLTAMP | 2008 | 8.5 | 2.125 | 16181.025 | 64755.38 | 257.72 | 2693.565 | 2.72 | 5 | 9 | 5 | 0.5555555556 | 1.28 | 1.8 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 0.5555555556 | 1.28 | 1.8 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.28 | 0.5555555556 | 1.838235294 | 1 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
323 | JN.21071 | 10 MVA | 132KV/6.9KV | VOLTAMP | 2008 | 8.1 | 7.776 | 14971.311 | 63932.085 | 96.876 | 1025.298 | 6.966 | 6 | 1.863 | 6 | 3.220611916 | 0.8958333333 | 0.3105 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 3.220611916 | 0.8958333333 | 0.3105 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.8958333333 | 3.220611916 | 0.8613264427 | 1 | Arching | Arching | Arching | Thermal Decomposition,corona
324 | B-30653 | 275 MVA | (420/√3)/11.5 KV | ALSTOM | 2012 | 8.1 | 4.698 | 15589.827 | 63620.478 | 64.962 | 746.415 | 3.969 | 9 | 5 | 7 | 1.4 | 0.8448275862 | 0.5555555556 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1.4 | 0.8448275862 | 0.5555555556 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.8448275862 | 1.4 | 1.76366843 | 1.285714286 | Arching | Arching | Arching | Thermal Decomposition,corona
325 | B-30657 | 275 MVA | (420/√3)/11.5 KV | ALSTOM | 2013 | 8.3 | 2.905 | 17068.203 | 64381.523 | 60.756 | 633.705 | 12.948 | 7 | 21.165 | 14 | 0.661469407 | 4.457142857 | 3.023571429 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Arching,Thermal Fault > 700 c | 0.661469407 | 4.457142857 | 3.023571429 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 4.457142857 | 0.661469407 | 1.081248069 | 0.5 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
326 | B-30651 | 275 MVA | (420/√3)/11.5 KV | ALSTOM | 2012 | 8.2 | 5.248 | 16043.054 | 64253.642 | 92.25 | 1067.968 | 9.184 | 8 | 1.886 | 7 | 3.711558855 | 1.75 | 0.23575 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 3.711558855 | 1.75 | 0.23575 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.75 | 3.711558855 | 0.762195122 | 1.142857143 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
327 | B-30654 | 275 MVA | (420/√3)/21 KV | ALSTOM | 2013 | 8 | 7.44 | 15229.44 | 63639.12 | 52.48 | 590.88 | 8 | 9 | 8 | 8 | 1 | 1.075268817 | 0.8888888889 | Arching | Low temperature thermal | Partial discharge, Normal | 1 | 1.075268817 | 0.8888888889 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.075268817 | 1 | 1 | 1.125 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
328 | B-30655 | 275 MVA | (420/√3)/21 KV | ALSTOM | 2013 | 8.2 | 6.97 | 16445.674 | 64114.57 | 64.206 | 709.464 | 2.87 | 7 | 9 | 5 | 0.5555555556 | 0.4117647059 | 1.285714286 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.5555555556 | 0.4117647059 | 1.285714286 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.4117647059 | 0.5555555556 | 1.742160279 | 1.4 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
329 | B-30656 | 275 MVA | (420/√3)/21 KV | ALSTOM | 2013 | 8.3 | 7.885 | 15948.035 | 65089.845 | 61.835 | 673.296 | 4.648 | 5 | 6 | 9 | 1.5 | 0.5894736842 | 1.2 | Arching | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 1.5 | 0.5894736842 | 1.2 | Discharge of Low Energy, | High Energy Discharge | Thermal Fault >700 c | 0.5894736842 | 1.5 | 1.936316695 | 0.5555555556 | Arching | Arching | Arching | Thermal Decomposition,corona
330 | 4644/1 | 15 MVA | 33/6.6 KV | BIPPL | 2015 | 7.9 | 6.794 | 15449.872 | 59661.906 | 244.031 | 2619.324 | 9.401 | 9 | 5 | 7 | 1.4 | 1.38372093 | 0.5555555556 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 1.4 | 1.38372093 | 0.5555555556 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.38372093 | 1.4 | 0.7446016381 | 1.285714286 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
331 | 4644/2 | 15 MVA | 33/6.6 KV | BIPPL | 2016 | 8.3 | 4.648 | 16943.454 | 61950.702 | 245.763 | 2664.715 | 9.047 | 9 | 8 | 4 | 0.5 | 1.946428571 | 0.8888888889 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 0.5 | 1.946428571 | 0.8888888889 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.946428571 | 0.5 | 0.4421355145 | 2.25 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
332 | 4696/2 | 40 MVA | 220/11 KV | BBL | 2002 | 7.9 | 1.817 | 15162.786 | 62022.189 | 60.514 | 625.285 | 4.108 | 7 | 5 | 3 | 0.6 | 2.260869565 | 0.7142857143 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 0.6 | 2.260869565 | 0.7142857143 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 2.260869565 | 0.6 | 0.7302823759 | 2.333333333 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
333 | 4696/2 | 40 MVA | 220/11 KV | BBL | 2002 | 8.1 | 1.944 | 16388.325 | 63074.214 | 72.576 | 746.334 | 5.265 | 5 | 8 | 8 | 1 | 2.708333333 | 1.6 | Arching | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 1 | 2.708333333 | 1.6 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 2.708333333 | 1 | 1.519468186 | 0.625 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
334 | 4696/1 | 40 MVA | 220/11 KV | BBL | 2002 | 8.5 | 3.655 | 15545.99 | 67562.675 | 77.775 | 821.525 | 2.805 | 6 | 8 | 6 | 0.75 | 0.7674418605 | 1.333333333 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.75 | 0.7674418605 | 1.333333333 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.7674418605 | 0.75 | 2.139037433 | 1 | Arching | Arching | Arching | Thermal Decomposition,corona
335 | 4696/1 | 40 MVA | 220/11 KV | BBL | 2002 | 8 | 8.4 | 15211.2 | 63358.56 | 84.4 | 881.76 | 6.96 | 8 | 9 | 8 | 0.8888888889 | 0.8285714286 | 1.125 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.8888888889 | 0.8285714286 | 1.125 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.8285714286 | 0.8888888889 | 1.149425287 | 1 | Arching | Arching | Arching | Thermal Decomposition,corona
336 | JN-21397/2 | 16 MVA | 11/3.6 KV | Voltamp | 2009 | 7.7 | 4.312 | 14356.342 | 60376.085 | 117.964 | 1280.895 | 62.678 | 16.093 | 138.446 | 123 | 0.8884330353 | 14.53571429 | 8.602870813 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Arching,Thermal Fault > 700 c | 0.8884330353 | 14.53571429 | 8.602870813 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 14.53571429 | 0.8884330353 | 1.962411053 | 0.1308373984 | Thermal Decomposition, | Arching | Arching | Arching
337 | JN-21397/2 | 16 MVA | 11/3.6 KV | Voltamp | 2009 | 8.1 | 6.966 | 16064.163 | 62631.954 | 123.282 | 1342.008 | 72.009 | 18.711 | 153.333 | 200 | 1.304350662 | 10.3372093 | 8.194805195 | Arching | Thermal Fault <700c, thermal fault >700c | Arching,Thermal Fault > 700 c | 1.304350662 | 10.3372093 | 8.194805195 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 10.3372093 | 1.304350662 | 2.777430599 | 0.093555 | Thermal Decomposition, | Arching | Arching | Arching
338 | JN-21397/4 | 16 MVA | 11/3.6 KV | Voltamp | 2009 | 7.5 | 6.45 | 16062.6 | 57164.775 | 82.35 | 889.95 | 3.15 | 9 | 6 | 8 | 1.333333333 | 0.488372093 | 0.6666666667 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1.333333333 | 0.488372093 | 0.6666666667 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.488372093 | 1.333333333 | 2.53968254 | 1.125 | Arching | Arching | Arching | Thermal Decomposition,corona
339 | JN-21397/3 | 16 MVA | 11/3.6 KV | Voltamp | 2009 | 8 | 1.28 | 16657.28 | 60921.2 | 116.16 | 1255.12 | 9 | 5 | 8 | 8 | 1 | 7.03125 | 1.6 | Arching | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 1 | 7.03125 | 1.6 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 7.03125 | 1 | 0.8888888889 | 0.625 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
340 | - | 270 MVA | 800/22 KV | HYUNDAI | 2012 | 8.3 | 2.656 | 17396.883 | 62756.549 | 141.764 | 1525.125 | 2.988 | 6 | 8 | 6 | 0.75 | 1.125 | 1.333333333 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 0.75 | 1.125 | 1.333333333 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.125 | 0.75 | 2.008032129 | 1 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
341 | 21704037TIG013-004 | 270 MVA | 800/22 KV | HYUNDAI | 2012 | 8.1 | 3.402 | 15111.036 | 63784.26 | 135.756 | 1411.587 | 1.863 | 2 | 9 | 4 | 0.4444444444 | 0.5476190476 | 4.5 | Partial discharge,Low Temprature thermal fault, | Low temperature thermal | Arching,Thermal Fault > 700 c | 0.4444444444 | 0.5476190476 | 4.5 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.5476190476 | 0.4444444444 | 2.147074611 | 0.5 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
342 | 20104037TIG010-002 | 270 MVA | 800/22 KV | HYUNDAI | 2012 | 8.1 | 5.265 | 16706.169 | 61774.569 | 137.781 | 1364.607 | 7.857 | 5 | 6 | 9 | 1.5 | 1.492307692 | 1.2 | Arching | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 1.5 | 1.492307692 | 1.2 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.492307692 | 1.5 | 1.145475372 | 0.5555555556 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
343 | 20104037TIG009-001 | 270 MVA | 800/22 KV | HYUNDAI | 2012 | 8.1 | 6.075 | 15265.584 | 63442.683 | 120.204 | 1002.294 | 4.941 | 7 | 5 | 5 | 1 | 0.8133333333 | 0.7142857143 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1 | 0.8133333333 | 0.7142857143 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.8133333333 | 1 | 1.011940903 | 1.4 | Arching | Arching | Arching | Thermal Decomposition,corona
344 | 20104037TIG010-003 | 270 MVA | 800/22 KV | HYUNDAI | 2012 | 8.3 | 3.652 | 16420.056 | 64298.855 | 134.792 | 1453.247 | 2.739 | 8 | 4 | 9 | 2.25 | 0.75 | 0.5 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 2.25 | 0.75 | 0.5 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.75 | 2.25 | 3.285870756 | 0.8888888889 | Arching | Arching | Arching | Thermal Decomposition,corona
345 | 20104037TIG013-001 | 270 MVA | 800/22 KV | HYUNDAI | 2012 | 7.9 | 5.688 | 15545.462 | 61082.721 | 111.311 | 1200.247 | 8 | 9 | 8 | 4 | 0.5 | 1.406469761 | 0.8888888889 | Partial discharge,Low Temprature thermal fault, | Low temperature thermal | Partial discharge, Normal | 0.5 | 1.406469761 | 0.8888888889 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.406469761 | 0.5 | 0.5 | 2.25 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
346 | 20104037TIG008-001 | 270 MVA | 800/22 KV | HYUNDAI | 2012 | 7.9 | 5.925 | 16278.661 | 60555.712 | 110.126 | 1142.182 | 5.609 | 9 | 5 | 8 | 1.6 | 0.9466666667 | 0.5555555556 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1.6 | 0.9466666667 | 0.5555555556 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.9466666667 | 1.6 | 1.426279194 | 1.125 | Arching | Arching | Arching | Thermal Decomposition,corona
347 | 20104037TIG008-002 | 270 MVA | 800/22 KV | HYUNDAI | 2012 | 8.5 | 5.44 | 17801.72 | 65757.275 | 105.995 | 891.055 | 2.89 | 7 | 9 | 8 | 0.8888888889 | 0.53125 | 1.285714286 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.8888888889 | 0.53125 | 1.285714286 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.53125 | 0.8888888889 | 2.76816609 | 0.875 | Arching | Arching | Arching | Thermal Decomposition,corona
348 | 20104037TIG011-002 | 270 MVA | 800/22 KV | HYUNDAI | 2012 | 8.4 | 2.94 | 16325.904 | 65061.612 | 118.272 | 1426.824 | 1.764 | 6 | 1.596 | 2 | 1.253132832 | 0.6 | 0.266 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1.253132832 | 0.6 | 0.266 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.6 | 1.253132832 | 1.133786848 | 3 | Arching | Arching | Arching | Thermal Decomposition,corona
349 | 20109037TIG013-002 | 270 MVA | 800/22 KV | HYUNDAI | 2012 | 7.6 | 7.524 | 14179.016 | 59891.344 | 115.368 | 1288.124 | 6.84 | 4 | 8 | 4 | 0.5 | 0.9090909091 | 2 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.5 | 0.9090909091 | 2 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.9090909091 | 0.5 | 0.5847953216 | 1 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
350 | 20104037TIG009-003 | 270 MVA | 800/22 KV | HYUNDAI | 2012 | 7.8 | 5.304 | 15835.482 | 60022.638 | 117.468 | 1188.876 | 8.658 | 7 | 1.248 | 7 | 5.608974359 | 1.632352941 | 0.1782857143 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 5.608974359 | 1.632352941 | 0.1782857143 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | Partial Discharges, | 1.632352941 | 5.608974359 | 0.8085008085 | 1 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
351 | 20104037TIG010-001 | 270 MVA | 800/22 KV | HYUNDAI | 2012 | 7.9 | 6.794 | 13842.143 | 62812.584 | 140.383 | 1332.572 | 9.243 | 8 | 8 | 2 | 0.25 | 1.360465116 | 1 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 0.25 | 1.360465116 | 1 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.360465116 | 0.25 | 0.2163799632 | 4 | Thermal Decomposition, | Thermal Decomposition, | Thermal Decomposition,corona | Thermal Decomposition,corona
352 | -- | 270 MVA | 800/22 KV | HYUNDAI | 2011 | 8.3 | 1.411 | 15897.737 | 65065.858 | 109.477 | 1128.551 | 8.632 | 4 | 1.245 | 9 | 7.228915663 | 6.117647059 | 0.31125 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 7.228915663 | 6.117647059 | 0.31125 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 6.117647059 | 7.228915663 | 1.042632067 | 0.4444444444 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
353 | 20104037TIG011-003 | 270 MVA | 800/22 KV | HYUNDAI | 2011 | 8.3 | 3.071 | 16509.613 | 64537.065 | 103.833 | 1147.724 | 11.039 | 8 | 8 | 2 | 0.25 | 3.594594595 | 1 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 0.25 | 3.594594595 | 1 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 3.594594595 | 0.25 | 0.1811758311 | 4 | Thermal Decomposition, | Thermal Decomposition, | Thermal Decomposition,corona | Thermal Decomposition,corona
354 | -- | 270 MVA | 800/22 KV | HYUNDAI | 2011 | 8.5 | 8.16 | 17048.875 | 65579.625 | 132.09 | 1385.585 | 10.965 | 8 | 7 | 9 | 1.285714286 | 1.34375 | 0.875 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 1.285714286 | 1.34375 | 0.875 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.34375 | 1.285714286 | 0.8207934337 | 0.8888888889 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
355 | 20109037TIG004-001 | 270 MVA | 800/22 KV | HYUNDAI | 2012 | 8.2 | 2.624 | 16669.616 | 62508.354 | 144.648 | 1531.268 | 11.726 | 8 | 2.87 | 8 | 2.787456446 | 4.46875 | 0.35875 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 2.787456446 | 4.46875 | 0.35875 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 4.46875 | 2.787456446 | 0.6822445847 | 1 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
356 | 20104037TIG004-003 | 270 MVA | 800/22 KV | HYUNDAI | 2012 | 8.8 | 1 | 18460.112 | 67597.024 | 109.472 | 1145.408 | 2.024 | 8 | 9 | 7 | 0.7777777778 | 2.024 | 1.125 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 0.7777777778 | 2.024 | 1.125 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 2.024 | 0.7777777778 | 3.458498024 | 1.142857143 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
357 | 20104037TIG004-004 | 270 MVA | 800/22 KV | HYUNDAI | 2012 | 8.2 | 2.46 | 16081.676 | 63653.894 | 96.432 | 1227.458 | 8 | 9 | 3.772 | 5 | 1.325556734 | 3.25203252 | 0.4191111111 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 1.325556734 | 3.25203252 | 0.4191111111 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 3.25203252 | 1.325556734 | 0.625 | 1.8 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
358 | 2029844 | 50 MVA | 66/6.9 KV | BHEL | 2011 | 7.9 | 0.948 | 14545.796 | 62367.024 | 112.259 | 1097.231 | 1.817 | 9 | 8 | 9 | 1.125 | 1.916666667 | 0.8888888889 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 1.125 | 1.916666667 | 0.8888888889 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.916666667 | 1.125 | 4.953219593 | 1 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
359 | 2029844 | 50 MVA | 66/6.9 KV | BHEL | 2011 | 8.1 | 0.972 | 14672.502 | 64094.409 | 118.665 | 1143.072 | 1.863 | 8 | 7 | 5 | 0.7142857143 | 1.916666667 | 0.875 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 0.7142857143 | 1.916666667 | 0.875 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.916666667 | 0.7142857143 | 2.683843264 | 1.6 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
360 | 2029844 | 50 MVA | 66/6.9 KV | BHEL | 2011 | 7.5 | 2.7 | 16332.975 | 57423.075 | 52.95 | 608.4 | 5 | 9 | 7 | 8 | 1.142857143 | 1.851851852 | 0.7777777778 | Arching | Low temperature thermal | Partial discharge, Normal | 1.142857143 | 1.851851852 | 0.7777777778 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.851851852 | 1.142857143 | 1.6 | 1.125 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
361 | 2029845 | 50 MVA | 66/6.9KV | BHEL | 2011 | 7.9 | 0.948 | 14000.538 | 63015.061 | 130.982 | 1360.617 | 7 | 6 | 6 | 4 | 0.6666666667 | 7.383966245 | 1 | Partial discharge,Low Temprature thermal fault, | Low temperature thermal | Low Temprature thermal Fault,Thermal Fault<700c | 0.6666666667 | 7.383966245 | 1 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 7.383966245 | 0.6666666667 | 0.5714285714 | 1.5 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
362 | 2029845 | 50 MVA | 66/6.9KV | BHEL | 2011 | 8 | 1.84 | 14659.52 | 63312.64 | 136.16 | 1383.12 | 6 | 9 | 5 | 7 | 1.4 | 3.260869565 | 0.5555555556 | Arching | Low temperature thermal | Partial discharge, Normal | 1.4 | 3.260869565 | 0.5555555556 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 3.260869565 | 1.4 | 1.166666667 | 1.285714286 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
363 | 2029845 | 50 MVA | 66/6.9KV | BHEL | 2011 | 8.2 | 1.886 | 15649.7 | 63916.376 | 116.522 | 1248.122 | 9 | 6 | 9 | 3 | 0.3333333333 | 4.772004242 | 1.5 | Partial discharge,Low Temprature thermal fault, | Low temperature thermal | Low Temprature thermal Fault,Thermal Fault<700c | 0.3333333333 | 4.772004242 | 1.5 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 4.772004242 | 0.3333333333 | 0.3333333333 | 2 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
364 | 10276 | 10 MVA | 66/11 KV | -- | 2011 | 7.6 | 1.748 | 14169.972 | 59456.776 | 107.236 | 1413.296 | 7 | 5 | 6 | 9 | 1.5 | 4.004576659 | 1.2 | Arching | Low temperature thermal | Low Temprature thermal Fault,Thermal Fault<700c | 1.5 | 4.004576659 | 1.2 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 4.004576659 | 1.5 | 1.285714286 | 0.5555555556 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
365 | 10276 | 10 MVA | 66/11 KV | -- | 2011 | 7.4 | 1.702 | 13971.348 | 57815.386 | 101.01 | 1369.74 | 6 | 9 | 9 | 3 | 0.3333333333 | 3.525264395 | 1 | Partial discharge,Low Temprature thermal fault, | Low temperature thermal | Low Temprature thermal Fault,Thermal Fault<700c | 0.3333333333 | 3.525264395 | 1 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 3.525264395 | 0.3333333333 | 0.5 | 3 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
366 | 10276 | 10 MVA | 66/11 KV | -- | 2011 | 6.5 | 4.095 | 12402.13 | 51433.785 | 44.72 | 469.495 | 4 | 5 | 9 | 9 | 1 | 0.9768009768 | 1.8 | Arching | Low temperature thermal | Low Temprature thermal Fault,Thermal Fault<700c | 1 | 0.9768009768 | 1.8 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.9768009768 | 1 | 2.25 | 0.5555555556 | Arching | Arching | Arching | Thermal Decomposition,corona
367 | 683000445 | 25 MVA | 6.6/6.9KV | SCHINEIDER | -- | 8.2 | 5.166 | 16708.566 | 62942.052 | 131.446 | 1471.572 | 6 | 8 | 7 | 4 | 0.5714285714 | 1.161440186 | 0.875 | Partial discharge,Low Temprature thermal fault, | Low temperature thermal | Partial discharge, Normal | 0.5714285714 | 1.161440186 | 0.875 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.161440186 | 0.5714285714 | 0.6666666667 | 2 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
368 | 683000445 | 25 MVA | 6.6/6.9KV | SCHINEIDER | -- | 8 | 6.08 | 13869.36 | 64659.6 | 75.44 | 805.68 | 44.8 | 5 | 5 | 9 | 1.8 | 7.368421053 | 1 | Arching | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 1.8 | 7.368421053 | 1 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 7.368421053 | 1.8 | 0.2008928571 | 0.5555555556 | Thermal Decomposition, | Arching | Thermal Decomposition,corona | Thermal Decomposition,corona
369 | 683000445 | 25 MVA | 6.6/6.9KV | SCHINEIDER | -- | 8.2 | 6.396 | 16251.58 | 63100.312 | 131.282 | 1434.59 | 8 | 8 | 8 | 9 | 1.125 | 1.250781739 | 1 | Arching | Low temperature thermal | Low Temprature thermal Fault,Thermal Fault<700c | 1.125 | 1.250781739 | 1 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.250781739 | 1.125 | 1.125 | 0.8888888889 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
370 | 621000403/1 | 25MVA | 11KV | AREVA | 2011 | 8.5 | 1.615 | 16567.265 | 65972.58 | 124.185 | 1414.825 | 9 | 6 | 10 | 9 | 0.9 | 5.572755418 | 1.666666667 | Partial discharge,Low Temprature thermal fault, | Low temperature thermal | Low Temprature thermal Fault,Thermal Fault<700c | 0.9 | 5.572755418 | 1.666666667 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 5.572755418 | 0.9 | 1 | 0.6666666667 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
371 | 621000403/1 | 25MVA | 11KV | AREVA | 2011 | 8.4 | 1.932 | 16923.396 | 64592.052 | 130.872 | 1421.7 | 6 | 8 | 8 | 6 | 0.75 | 3.105590062 | 1 | Partial discharge,Low Temprature thermal fault, | Low temperature thermal | Low Temprature thermal Fault,Thermal Fault<700c | 0.75 | 3.105590062 | 1 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 3.105590062 | 0.75 | 1 | 1.333333333 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
372 | JN-22633/1 | 25MVA | 66/11.5KV | VOLTAMP | 2017 | 8.1 | 3 | 12949.875 | 65539.935 | 126.036 | 1315.521 | 5 | 9 | 7 | 8 | 1.142857143 | 1.666666667 | 0.7777777778 | Arching | Arching | Partial discharge, Normal | 1.142857143 | 1.666666667 | 0.7777777778 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.666666667 | 1.142857143 | 1.6 | 1.125 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
373 | JN-22633/1 | 25MVA | 66/11.5KV | VOLTAMP | 2017 | 8.3 | 5 | 16975.824 | 64113.931 | 133.713 | 1346.343 | 6 | 7 | 5 | 9 | 1.8 | 1.2 | 0.7142857143 | Arching | Arching | Partial discharge, Normal | 1.8 | 1.2 | 0.7142857143 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.2 | 1.8 | 1.5 | 0.7777777778 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
374 | JN-22633/2 | 25MVA | 66/11.5KV | VOLTAMP | 2017 | 8.2 | 7 | 13422.088 | 66525.78 | 102.91 | 1083.548 | 5 | 9 | 8 | 8 | 1 | 0.7142857143 | 0.8888888889 | Arching | Arching | Partial discharge, Normal | 1 | 0.7142857143 | 0.8888888889 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.7142857143 | 1 | 1.6 | 1.125 | Arching | Arching | Arching | Thermal Decomposition,corona
375 | JN-22633/2 | 25MVA | 66/11.5KV | VOLTAMP | 2017 | 8.2 | 6 | 10786.116 | 68862.78 | 106.764 | 1135.29 | 7 | 8 | 9 | 9 | 1 | 1.166666667 | 1.125 | Arching | Arching | Low Temprature thermal Fault,Thermal Fault<700c | 1 | 1.166666667 | 1.125 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.166666667 | 1 | 1.285714286 | 0.8888888889 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
376 | JN-8103/4 | 25 MVA | 66/11 KV | VOLTAMP | 2002 | 7.8 | 55.068 | 14179.932 | 61003.644 | 190.398 | 1966.9338 | 22.464 | 7 | 35.49 | 22.386 | 0.6307692308 | 0.4079320113 | 5.07 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Arching,Thermal Fault > 700 c | 0.6307692308 | 0.4079320113 | 5.07 | High Energy Discharges | High Energy Discharge | Thermal Fault >700 c | 0.4079320113 | 0.6307692308 | 0.9965277778 | 0.3126954346 | Arching | Thermal Decomposition, | Arching | Arching
377 | JN-8103/3 | 25 MVA | 66/11 KV | VOLTAMP | 2002 | 8.3 | 50.713 | 17136.263 | 62476.175 | 191.813 | 1998.557 | 23.157 | 14 | 32.785 | 27.473 | 0.8379746835 | 0.4566284779 | 2.341785714 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.8379746835 | 0.4566284779 | 2.341785714 | High Energy Discharges | High Energy Discharge | Thermal Fault >700 c | 0.4566284779 | 0.8379746835 | 1.186379928 | 0.509591235 | Arching | Arching | Arching | Thermal Decomposition,corona
378 | LEL-109409 | 13 MVA | 33/3.3 KV | Siemens | 2010 | 8.1 | 4.536 | 15840.036 | 63351.963 | 108.945 | 1152.225 | 3.078 | 9 | 9 | 4 | 0.4444444444 | 0.6785714286 | 1 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.4444444444 | 0.6785714286 | 1 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.6785714286 | 0.4444444444 | 1.299545159 | 2.25 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
379 | LEL-109408 | 13 MVA | 33/3.3 KV | Siemens | 2010 | 7.9 | 2.765 | 15451.531 | 61098.284 | 123.714 | 1455.575 | 6.794 | 7 | 6 | 3 | 0.5 | 2.457142857 | 0.8571428571 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 0.5 | 2.457142857 | 0.8571428571 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 2.457142857 | 0.5 | 0.4415660877 | 2.333333333 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
380 | -- | 13 MVA | 33/3.3 KV | Siemens | 2010 | 7.9 | 2.923 | 15620.038 | 61254.941 | 105.544 | 1170.464 | 8 | 7 | 8 | 7 | 0.875 | 2.736914129 | 1.142857143 | Partial discharge,Low Temprature thermal fault, | Low temperature thermal | Low Temprature thermal Fault,Thermal Fault<700c | 0.875 | 2.736914129 | 1.142857143 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 2.736914129 | 0.875 | 0.875 | 1 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
381 | -- | 13 MVA | 33/3.3 KV | Siemens | 2010 | 8.2 | 6.97 | 16583.27 | 63266.444 | 119.392 | 1272.722 | 1.886 | 6 | 8 | 9 | 1.125 | 0.2705882353 | 1.333333333 | Arching | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 1.125 | 0.2705882353 | 1.333333333 | Discharge of Low Energy, | High Energy Discharge | Thermal Fault >700 c | 0.2705882353 | 1.125 | 4.772004242 | 0.6666666667 | Arching | Arching | Arching | Thermal Decomposition,corona
382 | -- | 13 MVA | 33/3.3 KV | Siemens | 2010 | 8.5 | 6.12 | 17355.045 | 65430.025 | 110.245 | 1201.22 | 9 | 9 | 8 | 8 | 1 | 1.470588235 | 0.8888888889 | Arching | Low temperature thermal | Partial discharge, Normal | 1 | 1.470588235 | 0.8888888889 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.470588235 | 1 | 0.8888888889 | 1.125 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
383 | LEL-109404 | 13 MVA | 33/3.3 KV | Siemens | 2010 | 8 | 9.12 | 17496.64 | 60945.6 | 82.96 | 991.52 | 7 | 6 | 9 | 8 | 0.8888888889 | 0.7675438596 | 1.5 | Partial discharge,Low Temprature thermal fault, | Low temperature thermal | Low Temprature thermal Fault,Thermal Fault<700c | 0.8888888889 | 0.7675438596 | 1.5 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.7675438596 | 0.8888888889 | 1.142857143 | 0.75 | Arching | Arching | Arching | Thermal Decomposition,corona
384 | 2213/48 | 15 MVA | 33/6.6 KV | English Electrical | -- | 8 | 2 | 16212.88 | 60781.68 | 218.32 | 2235.92 | 5.44 | 8 | 6 | 6 | 1 | 2.72 | 0.75 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 1 | 2.72 | 0.75 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 2.72 | 1 | 1.102941176 | 1.333333333 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
385 | 2213/48 | 15 MVA | 33/6.6 KV | English Electrical | 1936 | 8.6 | 2 | 15837.932 | 65614.732 | 96.836 | 1082.912 | 5 | 6 | 9 | 4 | 0.4444444444 | 2.5 | 1.5 | Partial discharge,Low Temprature thermal fault, | Arching | Low Temprature thermal Fault,Thermal Fault<700c | 0.4444444444 | 2.5 | 1.5 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 2.5 | 0.4444444444 | 0.8 | 1.5 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
386 | B-27471 | 10 MVA | 33/6.6 KV | GEC | 1980 | 8.4 | 25.368 | 14310.324 | 66929.268 | 167.664 | 1793.904 | 15.036 | 9.072 | 57.204 | 45 | 0.7866582756 | 0.5927152318 | 6.305555556 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Arching,Thermal Fault > 700 c | 0.7866582756 | 0.5927152318 | 6.305555556 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.5927152318 | 0.7866582756 | 2.992817239 | 0.2016 | Arching | Arching | Arching | Arching
387 | 7339824/1 | 16 MVA | 33/6.6 KV | SCHNEIDER | 2017 | 8.1 | 8.019 | 15904.998 | 62388.711 | 143.046 | 1519.236 | 6.399 | 8 | 8 | 7 | 0.875 | 0.797979798 | 1 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.875 | 0.797979798 | 1 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.797979798 | 0.875 | 1.093920925 | 1.142857143 | Arching | Arching | Arching | Thermal Decomposition,corona
388 | 220875172/01 | 16 MVA | 33/6.6 KV | SCHNEIDER | 2018 | 8.2 | 6.15 | 15773.93 | 63846.922 | 133.004 | 1413.024 | 7 | 7 | 7 | 8 | 1.142857143 | 1.138211382 | 1 | Arching | Low temperature thermal | Low Temprature thermal Fault,Thermal Fault<700c | 1.142857143 | 1.138211382 | 1 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.138211382 | 1.142857143 | 1.142857143 | 0.875 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
389 | 2019454 | 40 MVA | 220/33 KV | BHEL | 2008 | 7.9 | 4.345 | 14745.666 | 62854.059 | 62.884 | 719.848 | 8 | 6 | 6 | 9 | 1.5 | 1.841196778 | 1 | Arching | Low temperature thermal | Low Temprature thermal Fault,Thermal Fault<700c | 1.5 | 1.841196778 | 1 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.841196778 | 1.5 | 1.125 | 0.6666666667 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
390 | 2019455 | 40 MVA | 220/33 KV | BHEL | 2008 | 8.2 | 5.904 | 16446.248 | 64232.65 | 61.746 | 737.672 | 3.69 | 9 | 9 | 7 | 0.7777777778 | 0.625 | 1 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.7777777778 | 0.625 | 1 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.625 | 0.7777777778 | 1.89701897 | 1.285714286 | Arching | Arching | Arching | Thermal Decomposition,corona
391 | 2019003 | 16 MVA | 10.5/6.9 KV | BHEL | 2007 | 8.2 | 6.97 | 15280.7 | 64410.098 | 110.864 | 1308.392 | 3.198 | 7 | 6 | 6 | 1 | 0.4588235294 | 0.8571428571 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1 | 0.4588235294 | 0.8571428571 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.4588235294 | 1 | 1.876172608 | 1.166666667 | Arching | Arching | Arching | Thermal Decomposition,corona
392 | 2019004 | 16 MVA | 10.5/6.9 KV | BHEL | 2007 | 7.8 | 6.708 | 15703.272 | 60180.666 | 103.116 | 1135.368 | 4.914 | 5 | 9 | 8 | 0.8888888889 | 0.7325581395 | 1.8 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.8888888889 | 0.7325581395 | 1.8 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.7325581395 | 0.8888888889 | 1.628001628 | 0.625 | Arching | Arching | Arching | Thermal Decomposition,corona
393 | B-29914 | 24 MVA | 33/0.25 KV | Alstom | 2005 | 8 | 5.92 | 15425.2 | 62150.72 | 98.72 | 1340.24 | 5.68 | 6 | 6 | 3 | 0.5 | 0.9594594595 | 1 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.5 | 0.9594594595 | 1 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.9594594595 | 0.5 | 0.5281690141 | 2 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
394 | 7644/1 | 11 MVA | 33/11 KV | CGL | 2013 | 8.3 | 4.648 | 16712.548 | 63630.705 | 129.314 | 1354.975 | 3.237 | 8 | 5 | 4 | 0.8 | 0.6964285714 | 0.625 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Partial discharge, Normal | 0.8 | 0.6964285714 | 0.625 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.6964285714 | 0.8 | 1.235712079 | 2 | Arching | Arching | Arching | Thermal Decomposition,corona
395 | T-09825/1 | 10 MVA | 140.4/7.02 KV | CGL | 2010 | 7.9 | 1.817 | 13439.401 | 63936.912 | 79.316 | 878.875 | 8 | 7 | 6 | 7 | 1.166666667 | 4.40286186 | 0.8571428571 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1.166666667 | 4.40286186 | 0.8571428571 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 4.40286186 | 1.166666667 | 0.875 | 1 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
396 | 2094 | 16/20 MVA | 6.6 KV | EMCO | 2008 | 8.1 | 6.885 | 15926.949 | 63122.085 | 117.045 | 1275.345 | 5.508 | 6 | 5 | 9 | 1.8 | 0.8 | 0.8333333333 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1.8 | 0.8 | 0.8333333333 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.8 | 1.8 | 1.633986928 | 0.6666666667 | Arching | Arching | Arching | Thermal Decomposition,corona
397 | 20150686TIG003 | 270 MVA | 765/22 KV | -- | -- | 8.5 | 4 | 15341.82 | 68040.12 | 71.485 | 829.09 | 8 | 7 | 7 | 9 | 1.285714286 | 2 | 1 | Arching | Arching | Low Temprature thermal Fault,Thermal Fault<700c | 1.285714286 | 2 | 1 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 2 | 1.285714286 | 1.125 | 0.7777777778 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
398 | 20104037TIG013-002 | 270 MVA | 765/22 KV | Hyundai | 2011 | 8.1 | 4.455 | 16069.023 | 63258.003 | 104.814 | 1112.373 | 5.103 | 9 | 4 | 8 | 2 | 1.145454545 | 0.4444444444 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 2 | 1.145454545 | 0.4444444444 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.145454545 | 2 | 1.567705271 | 1.125 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
399 | 20104037TIG009-003 | 270 MVA | 765/22 KV | HYUNDAI | 2012 | 8.1 | 452.709 | 11598.876 | 57676.293 | 160.137 | 1726.596 | 2750.598 | 323.352 | 3176.739 | 2051.487 | 0.6457839313 | 6.075863303 | 9.824398798 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Arching,Thermal Fault > 700 c | 0.6457839313 | 6.075863303 | 9.824398798 | High Energy Discharges | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 6.075863303 | 0.6457839313 | 0.7458330879 | 0.157618352 | Thermal Decomposition, | Thermal Decomposition, | Arching | Arching
400 | T09548/4 | 80 MVA | 141.2/35.3/11.710 KV | CGL | 2010 | 8 | 4.16 | 15336.48 | 62380.88 | 126.96 | 1403.68 | 33.92 | 9.84 | 23.92 | 33 | 1.379598662 | 8.153846154 | 2.430894309 | Arching | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 1.379598662 | 8.153846154 | 2.430894309 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 8.153846154 | 1.379598662 | 0.9728773585 | 0.2981818182 | Thermal Decomposition, | Arching | Arching | Arching
401 | 6005784 | 50/75/130 MVA | 220/132KKV | BHEL | 1999 | 7.2 | 6.984 | 13575.888 | 56319.12 | 135 | 1423.44 | 8.496 | 3.6 | 2.52 | 23 | 9.126984127 | 1.216494845 | 0.7 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 9.126984127 | 1.216494845 | 0.7 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.216494845 | 9.126984127 | 2.707156309 | 0.1565217391 | Thermal Decomposition, | Arching | Arching | Arching
402 | 6005784 | 50/75/130 MVA | 220/132KKV | BHEL | 1999 | 7.9 | 26.623 | 15958.869 | 60216.486 | 156.578 | 1781.45 | 6.636 | 11.455 | 7.189 | 7 | 0.9737098345 | 0.2492581602 | 0.6275862069 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Partial discharge, Normal | 0.9737098345 | 0.2492581602 | 0.6275862069 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.2492581602 | 0.9737098345 | 1.054852321 | 1.636428571 | Arching | Arching | Arching | Thermal Decomposition,corona
403 | 6005784 | 50/75/130 MVA | 220/132KKV | BHEL | 1999 | 7.7 | 8.547 | 15074.521 | 59229.709 | 132.594 | 1479.94 | 9.317 | 7.469 | 11.396 | 9 | 0.7897507898 | 1.09009009 | 1.525773196 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 0.7897507898 | 1.09009009 | 1.525773196 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.09009009 | 0.7897507898 | 0.9659761726 | 0.8298888889 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
404 | 6005784 | 50/75/130 MVA | 220/132KKV | BHEL | 1999 | 7.2 | 15.624 | 11656.296 | 57702.456 | 129.024 | 1534.464 | 9.576 | 8.136 | 5.832 | 7 | 1.200274348 | 0.6129032258 | 0.7168141593 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1.200274348 | 0.6129032258 | 0.7168141593 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.6129032258 | 1.200274348 | 0.730994152 | 1.162285714 | Arching | Arching | Arching | Thermal Decomposition,corona
405 | 6005785 | 50/75/130 MVA | 220/132KKV | BHEL | 1999 | 7 | 5.32 | 13231.61 | 54236.14 | 144.62 | 1627.92 | 6.65 | 9 | 3.57 | 2 | 0.5602240896 | 1.25 | 0.3966666667 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 0.5602240896 | 1.25 | 0.3966666667 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.25 | 0.5602240896 | 0.3007518797 | 4.5 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
406 | 6005785 | 50/75/130 MVA | 220/132KKV | BHEL | 1999 | 8 | 13.28 | 16320.64 | 60944.72 | 167.44 | 1680.24 | 8.08 | 8 | 2.88 | 4 | 1.388888889 | 0.6084337349 | 0.36 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1.388888889 | 0.6084337349 | 0.36 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.6084337349 | 1.388888889 | 0.495049505 | 2 | Arching | Arching | Arching | Thermal Decomposition,corona
407 | 6005785 | 50/75/130 MVA | 220/132KKV | BHEL | 1999 | 8.1 | 21.141 | 17428.932 | 61520.877 | 136.161 | 1474.2 | 6.399 | 7 | 2.916 | 5 | 1.714677641 | 0.3026819923 | 0.4165714286 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1.714677641 | 0.3026819923 | 0.4165714286 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.3026819923 | 1.714677641 | 0.7813720894 | 1.4 | Arching | Arching | Arching | Thermal Decomposition,corona
408 | 6005785 | 50/75/130 MVA | 220/132KKV | BHEL | 1999 | 7.3 | 18.834 | 13301.549 | 57281.64 | 111.544 | 1192.017 | 8.176 | 6 | 2.628 | 5 | 1.902587519 | 0.4341085271 | 0.438 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1.902587519 | 0.4341085271 | 0.438 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.4341085271 | 1.902587519 | 0.6115459883 | 1.2 | Arching | Arching | Arching | Thermal Decomposition,corona
409 | 2005423 | 80 MVA | 132 /11.5 KV | BHARAT BIJLEE | 1989 | 7.8 | 19.266 | 12153.18 | 63337.404 | 157.326 | 1645.956 | 31.824 | 46.722 | 12.246 | 33 | 2.694757472 | 1.651821862 | 0.2621035058 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 2.694757472 | 1.651821862 | 0.2621035058 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.651821862 | 2.694757472 | 1.036953243 | 1.415818182 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
410 | 2010654 | 50 MVA | 132 /11 KV | BHEL | 1997 | 7.4 | 6.882 | 14724.224 | 57659.172 | 86.728 | 793.502 | 8.14 | 8 | 5.624 | 38 | 6.756756757 | 1.182795699 | 0.703 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 6.756756757 | 1.182795699 | 0.703 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.182795699 | 6.756756757 | 4.668304668 | 0.2105263158 | Thermal Decomposition, | Arching | Arching | Arching
411 | 2010653 | 16 MVA | 11 /6.9 KV | BHEL | 1997 | 8 | 9.2 | 16498.8 | 62103.44 | 83.68 | 846.48 | 10.56 | 9 | 7.52 | 9 | 1.196808511 | 1.147826087 | 0.8355555556 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 1.196808511 | 1.147826087 | 0.8355555556 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.147826087 | 1.196808511 | 0.8522727273 | 1 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
412 | 2010652 | 16 MVA | 11 /6.9 KV | BHEL | 1997 | 8.4 | 7.812 | 13813.716 | 67202.268 | 204.204 | 1733.844 | 7.056 | 6 | 1.932 | 7 | 3.623188406 | 0.9032258065 | 0.322 | Arching | Low temperature thermal | Partial discharge, Normal | 3.623188406 | 0.9032258065 | 0.322 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.9032258065 | 3.623188406 | 0.9920634921 | 0.8571428571 | Arching | Arching | Arching | Thermal Decomposition,corona
413 | 2010655 | 50 MVA | 132 /11 KV | BHEL | 1997 | 8 | 8 | 15791.12 | 62537.2 | 80.32 | 965.12 | 9.68 | 7.52 | 8 | 6 | 0.75 | 1.21 | 1.063829787 | Partial discharge,Low Temprature thermal fault, | Arching | Low Temprature thermal Fault,Thermal Fault<700c | 0.75 | 1.21 | 1.063829787 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.21 | 0.75 | 0.6198347107 | 1.253333333 | Thermal Decomposition, | FALSE | Arching | Thermal Decomposition,corona
414 | 2800057667 | 28 MVA | 11 /0.360 KV | NGEF | 1999 | 7.8 | 1.092 | 13505.778 | 62645.778 | 137.982 | 849.654 | 8 | 7.41 | 19.422 | 15 | 0.7723200494 | 7.326007326 | 2.621052632 | Partial discharge,Low Temprature thermal fault, | Low temperature thermal | Low Temprature thermal Fault,Thermal Fault<700c | 0.7723200494 | 7.326007326 | 2.621052632 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 7.326007326 | 0.7723200494 | 1.875 | 0.494 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
415 | 2800049527 | 15 MVA | 11 /0.293 V | NGEF | 1989 | 8.6 | 1.806 | 17927.216 | 66049.204 | 85.054 | 880.984 | 9 | 9 | 7 | 6 | 0.8571428571 | 4.983388704 | 0.7777777778 | Partial discharge,Low Temprature thermal fault, | Low temperature thermal | Partial discharge, Normal | 0.8571428571 | 4.983388704 | 0.7777777778 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 4.983388704 | 0.8571428571 | 0.6666666667 | 1.5 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
416 | HT-1597/12313 | 28 MVA | 11 /0.360 KV | EMCO | 2003-4 | 8.4 | 4.704 | 18438.252 | 62682.564 | 146.16 | 1682.016 | 3.192 | 4.956 | 8 | 7 | 0.875 | 0.6785714286 | 1.614205004 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.875 | 0.6785714286 | 1.614205004 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.6785714286 | 0.875 | 2.192982456 | 0.708 | Arching | Arching | Arching | Thermal Decomposition,corona
417 | 5741/02 | 40 MVA | 132/11.5 KV | BHARAT BIJLEE | 2019 | 7.5 | 8 | 11013.675 | 62262.45 | 75.375 | 829.125 | 8 | 7 | 5 | 8 | 1.6 | 1 | 0.7142857143 | Arching | Arching | Partial discharge, Normal | 1.6 | 1 | 0.7142857143 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 1 | 1.6 | 1 | 0.875 | Arching | Arching | Arching | Thermal Decomposition,corona
418 | 5741/02 | 40 MVA | 132/11.5 KV | BHARAT BIJLEE | 2019 | 6.8 | 5 | 11462.012 | 55099.856 | 90.712 | 678.776 | 6 | 8 | 7 | 9 | 1.285714286 | 1.2 | 0.875 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 1.285714286 | 1.2 | 0.875 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.2 | 1.285714286 | 1.5 | 0.8888888889 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
419 | 5741/01 | 40 MVA | 132/11.5 KV | BHARAT BIJLEE | 2019 | 7.1 | 4 | 13150.904 | 56306.408 | 62.622 | 750.186 | 9 | 9 | 5 | 8 | 1.6 | 2.25 | 0.5555555556 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 1.6 | 2.25 | 0.5555555556 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 2.25 | 1.6 | 0.8888888889 | 1.125 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
420 | 5741/01 | 40 MVA | 132/11.5 KV | BHARAT BIJLEE | 2019 | 7.4 | 7 | 13093.634 | 59305.672 | 72.964 | 811.114 | 7 | 6 | 8 | 6 | 0.75 | 1 | 1.333333333 | Partial discharge,Low Temprature thermal fault, | Arching | Low Temprature thermal Fault,Thermal Fault<700c | 0.75 | 1 | 1.333333333 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 1 | 0.75 | 0.8571428571 | 1 | Arching | FALSE | Arching | Thermal Decomposition,corona
421 | -- | 15 MVA | 12.5/151 KV | AREVA | 2011 | 6.6 | 4 | 9735.924 | 54541.014 | 88.374 | 961.026 | 6 | 8 | 4 | 8 | 2 | 1.5 | 0.5 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 2 | 1.5 | 0.5 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.5 | 2 | 1.333333333 | 1 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
422 | 5079/02 | 16/21 MVA | 33/6.6 KV | BHARAT BIJLEE | 2009 | 7 | 5 | 13611.99 | 54564.79 | 70.63 | 744.31 | 0.91 | 6 | 9 | 6 | 0.6666666667 | 0.182 | 1.5 | Partial discharge,Low Temprature thermal fault, | Arching | Low Temprature thermal Fault,Thermal Fault<700c | 0.6666666667 | 0.182 | 1.5 | High Energy Discharge | Discharge of Low Energy | Thermal Fault >700 c | 0.182 | 0.6666666667 | 6.593406593 | 1 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
423 | 5079/01 | 16/21 MVA | 33/6.6 KV | BHARAT BIJLEE | 2009 | 8.1 | 3 | 12693.591 | 64827.702 | 258.147 | 2493.342 | 5 | 8 | 8 | 8 | 1 | 1.666666667 | 1 | Arching | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 1 | 1.666666667 | 1 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.666666667 | 1 | 1.6 | 1 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
424 | 3366/2 | 26.5 MVA | 33/6.9 KV | VOLTAMP | 1994 | 7.2 | 38.232 | 11561.544 | 57175.92 | 173.448 | 2050.416 | 94.608 | 214.848 | 5 | 66 | 13.2 | 2.474576271 | 0.0232722669 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 13.2 | 2.474576271 | 0.0232722669 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | Partial Discharges, | 2.474576271 | 13.2 | 0.6976154236 | 3.255272727 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
425 | JN-21313/2 | 10 MVA | 11/6.9 KV | VOLTAMP | 2009 | 8.1 | 11.502 | 15246.711 | 63559.242 | 146.934 | 1540.782 | 7 | 9 | 4 | 5 | 1.25 | 0.6085898105 | 0.4444444444 | Arching | Low temperature thermal | Partial discharge, Normal | 1.25 | 0.6085898105 | 0.4444444444 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.6085898105 | 1.25 | 0.7142857143 | 1.8 | Arching | Arching | Arching | Thermal Decomposition,corona
426 | JN-23491/1 | 16 MVA | 11/6.9 KV | VOLTAMP | 2021 | 8.5 | 5.015 | 13490.265 | 69785.765 | 59.415 | 952.765 | 9 | 9 | 7 | 6 | 0.8571428571 | 1.794616152 | 0.7777777778 | Partial discharge,Low Temprature thermal fault, | Low temperature thermal | Partial discharge, Normal | 0.8571428571 | 1.794616152 | 0.7777777778 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.794616152 | 0.8571428571 | 0.6666666667 | 1.5 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
427 | JN-3391/2 | 16 MVA | 11/6.9 KV | VOLTAMP | 1995 | 7.4 | 5.772 | 10213.998 | 61413.414 | 104.71 | 1160.172 | 11.1 | 6 | 9 | 7 | 0.7777777778 | 1.923076923 | 1.5 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 0.7777777778 | 1.923076923 | 1.5 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.923076923 | 0.7777777778 | 0.6306306306 | 0.8571428571 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
428 | JN-3392/1 | 10 MVA | 11/6.9 KV | VOLTAMP | 1995 | 7.5 | 4.05 | 13410.675 | 58000.65 | 216.675 | 2262.15 | 15 | 8 | 5 | 8 | 1.6 | 3.703703704 | 0.625 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 1.6 | 3.703703704 | 0.625 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 3.703703704 | 1.6 | 0.5333333333 | 1 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
429 | JN-3392/2 | 10 MVA | 11/6.9 KV | VOLTAMP | 1995 | 7.2 | 8.064 | 10588.032 | 58261.032 | 253.08 | 1498.104 | 77.832 | 65.232 | 491.976 | 15.336 | 0.0311722523 | 9.651785714 | 7.541942605 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Arching,Thermal Fault > 700 c | 0.0311722523 | 9.651785714 | 7.541942605 | Thermal Fault> 300c and<700 c | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 9.651785714 | 0.0311722523 | 0.197039778 | 4.253521127 | Thermal Decomposition, | Thermal Decomposition, | Thermal Decomposition,corona | Thermal Decomposition,corona
430 | KT-10000/19 | 10 MVA | 11/6.9 KV | KANOHAR | 2012 | 7.8 | 3 | 11469.51 | 64792.416 | 67.392 | 786.162 | 4 | 8 | 5 | 9 | 1.8 | 1.333333333 | 0.625 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 1.8 | 1.333333333 | 0.625 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.333333333 | 1.8 | 2.25 | 0.8888888889 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
431 | KT-10000/20 | 10 MVA | 11/6.9 KV | KANOHAR | 2012 | 8 | 4 | 12660.88 | 65375.84 | 88.72 | 820.64 | 7 | 9 | 7 | 6 | 0.8571428571 | 1.75 | 0.7777777778 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 0.8571428571 | 1.75 | 0.7777777778 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.75 | 0.8571428571 | 0.8571428571 | 1.5 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
432 | - | 16 MVA | 132/11 | GEC ALSTOM | - | 8 | 4.08 | 14673.2 | 62152.96 | 205.92 | 2485.12 | 10.24 | 2.72 | 4 | 7 | 1.75 | 2.509803922 | 1.470588235 | Arching | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 1.75 | 2.509803922 | 1.470588235 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 2.509803922 | 1.75 | 0.68359375 | 0.3885714286 | Thermal Decomposition, | Arching | Arching | Arching
433 | - | 16 MVA | 132/11 | GEC ALSTOM | - | 8.2 | 88.56 | 15176.478 | 63948.028 | 182.368 | 1793.422 | 43.542 | 18.86 | 39.77 | 62.566 | 1.573195876 | 0.4916666667 | 2.108695652 | Arching | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 1.573195876 | 0.4916666667 | 2.108695652 | Discharge of Low Energy, | High Energy Discharge | Thermal Fault >700 c | 0.4916666667 | 1.573195876 | 1.436911488 | 0.3014416776 | Arching | Arching | Arching | Arching
434 | 26898 | 16 MVA | 132/11 | MTPL | 2016 | 7.6 | 7.068 | 11234.472 | 63546.792 | 75.468 | 689.928 | 6.536 | 8 | 4.788 | 9 | 1.879699248 | 0.9247311828 | 0.5985 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1.879699248 | 0.9247311828 | 0.5985 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.9247311828 | 1.879699248 | 1.376988984 | 0.8888888889 | Arching | Arching | Arching | Thermal Decomposition,corona
435 | 26898 | 16 MVA | 132/11 | MTPL | 2016 | 7.4 | 7.548 | 11988.592 | 60912.508 | 66.748 | 75.702 | 9.102 | 9 | 7.4 | 11.618 | 1.57 | 1.205882353 | 0.8222222222 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 1.57 | 1.205882353 | 0.8222222222 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.205882353 | 1.57 | 1.276422764 | 0.7746600103 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
436 | TBI/623000451/2 | 16 MVA | 33/6.9 KV | SCHNEIDER ELECTRIC | 2012 | 8 | 12.48 | 12922.16 | 63866 | 182.88 | 2070.8 | 94.16 | 16.4 | 118.48 | 7 | 0.05908170155 | 7.544871795 | 7.224390244 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Arching,Thermal Fault > 700 c | 0.05908170155 | 7.544871795 | 7.224390244 | Thermal Fault> 300c and<700 c | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 7.544871795 | 0.05908170155 | 0.0743415463 | 2.342857143 | Thermal Decomposition, | Thermal Decomposition, | Thermal Decomposition,corona | Thermal Decomposition,corona
437 | JN-3166/3 | 26.5 MVA | 33/6.6 KV | VOLTAMP | 1994 | 8.4 | 7.056 | 15473.304 | 66296.664 | 130.452 | 1498.98 | 9.912 | 8.4 | 28.056 | 8 | 0.2851439977 | 1.404761905 | 3.34 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Arching,Thermal Fault > 700 c | 0.2851439977 | 1.404761905 | 3.34 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.404761905 | 0.2851439977 | 0.807102502 | 1.05 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
438 | JN-3366/2 | 26.5 MVA | 33/6.9 KV | VOLTAMP | 1994 | 8.6 | 32.938 | 14700.582 | 68231.196 | 177.848 | 1927.604 | 71.638 | 239.768 | 13.674 | 6 | 0.4387889425 | 2.174934726 | 0.05703012912 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 0.4387889425 | 2.174934726 | 0.05703012912 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Partial Discharges, | 2.174934726 | 0.4387889425 | 0.08375443201 | 39.96133333 | Thermal Decomposition, | Thermal Decomposition, | Thermal Decomposition,corona | Thermal Decomposition,corona
439 | JN-3166/1 | 26.5 MVA | 33/6.6 KV | VOLTAMP | 1994 | 7.2 | 6.336 | 12542.832 | 56754.72 | 135.072 | 1457.208 | 11.16 | 7.128 | 15.984 | 54 | 3.378378378 | 1.761363636 | 2.242424242 | Arching | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 3.378378378 | 1.761363636 | 2.242424242 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.761363636 | 3.378378378 | 4.838709677 | 0.132 | Thermal Decomposition, | Arching | Arching | Arching
440 | JN-3166 | 26.5 MVA | 33/66 KV | VOLTAMP | 1994 | 8.2 | 2.788 | 12277.45 | 67274.03 | 106.272 | 1159.972 | 8 | 6 | 7 | 6 | 0.8571428571 | 2.869440459 | 1.166666667 | Partial discharge,Low Temprature thermal fault, | Low temperature thermal | Low Temprature thermal Fault,Thermal Fault<700c | 0.8571428571 | 2.869440459 | 1.166666667 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 2.869440459 | 0.8571428571 | 0.75 | 1 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
441 | 3166/4 | 26.5 MVA | 33/66 KV | VOLTAMP | 1994 | 8.4 | 7.056 | 11922.876 | 69594.168 | 128.016 | 1382.388 | 6 | 8 | 8 | 7 | 0.875 | 0.8503401361 | 1 | Partial discharge,Low Temprature thermal fault, | Low temperature thermal | Low Temprature thermal Fault,Thermal Fault<700c | 0.875 | 0.8503401361 | 1 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.8503401361 | 0.875 | 1.166666667 | 1.142857143 | Arching | Arching | Arching | Thermal Decomposition,corona
442 | 5019/1 | 40 MVA | 33/11.5 KV | BBL | 2007 | 7.4 | 7.326 | 11411.466 | 59508.358 | 172.05 | 1814.258 | 5 | 9 | 5 | 8 | 1.6 | 0.6825006825 | 0.5555555556 | Arching | Low temperature thermal | Partial discharge, Normal | 1.6 | 0.6825006825 | 0.5555555556 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.6825006825 | 1.6 | 1.6 | 1.125 | Arching | Arching | Arching | Thermal Decomposition,corona
443 | 5019/2 | 40 MVA | 33/11.5 KV | BBL | 2007 | 8.2 | 4.592 | 12884.578 | 66853.862 | 147.436 | 1600.148 | 7 | 1.886 | 8 | 6 | 0.75 | 1.524390244 | 4.241781548 | Partial discharge,Low Temprature thermal fault, | Low temperature thermal | Arching,Thermal Fault > 700 c | 0.75 | 1.524390244 | 4.241781548 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.524390244 | 0.75 | 0.8571428571 | 0.3143333333 | Thermal Decomposition, | Arching | Arching | Arching
444 | 4246/3 | 26.5 MVA | 33/6.9 KV | VOLTAMP | 1997 | 8.4 | 4.956 | 13932.576 | 66816.372 | 154.98 | 1673.784 | 20.748 | 87.78 | 166.404 | 114 | 0.6850796856 | 4.186440678 | 1.89569378 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 0.6850796856 | 4.186440678 | 1.89569378 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 4.186440678 | 0.6850796856 | 5.494505495 | 0.77 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
445 | JN-4206/2 | 26.5 MVA | 33/6.9 KV | VOLTAMP | 1997 | 7.8 | 8.736 | 14640.288 | 61007.934 | 126.204 | 1568.424 | 8 | 9 | 7.332 | 4 | 0.545553737 | 0.9157509158 | 0.8146666667 | Partial discharge,Low Temprature thermal fault, | Low temperature thermal | Partial discharge, Normal | 0.545553737 | 0.9157509158 | 0.8146666667 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.9157509158 | 0.545553737 | 0.5 | 2.25 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
446 | JN-4206/01 | 26.5 MVA | 33/6.9 KV | VOLTAMP | 1997 | 8.4 | 4.704 | 15722.7 | 65932.608 | 162.372 | 1730.988 | 9 | 7 | 6 | 8 | 1.333333333 | 1.913265306 | 0.8571428571 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 1.333333333 | 1.913265306 | 0.8571428571 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.913265306 | 1.333333333 | 0.8888888889 | 0.875 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
447 | B-29514 | 10 MVA | - | - | - | 7.2 | 5.616 | 11743.488 | 58275.504 | 127.944 | 1405.512 | 7 | 9 | 7 | 9 | 1.285714286 | 1.246438746 | 0.7777777778 | Arching | Low temperature thermal | Partial discharge, Normal | 1.285714286 | 1.246438746 | 0.7777777778 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.246438746 | 1.285714286 | 1.285714286 | 1 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
448 | -- | 10 MVA | -- | CGL | 2010 | 7.7 | 0.847 | 12365.353 | 62448.617 | 86.471 | 989.758 | 6 | 6 | 9 | 8 | 0.8888888889 | 7.083825266 | 1.5 | Partial discharge,Low Temprature thermal fault, | Low temperature thermal | Low Temprature thermal Fault,Thermal Fault<700c | 0.8888888889 | 7.083825266 | 1.5 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 7.083825266 | 0.8888888889 | 1.333333333 | 0.75 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
450 | 90118B/06 | 70 MVA | 21/6.9 | TOSHIBA | 2015 | 8.5 | 6 | 9473.08 | 74121.105 | 76.84 | 687.14 | 8 | 5 | 8 | 2 | 0.25 | 1.333333333 | 1.6 | Partial discharge,Low Temprature thermal fault, | Arching | Low Temprature thermal Fault,Thermal Fault<700c | 0.25 | 1.333333333 | 1.6 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.333333333 | 0.25 | 0.25 | 2.5 | Thermal Decomposition, | Thermal Decomposition, | Thermal Decomposition,corona | Thermal Decomposition,corona
451 | 90118B/03 | 70 MVA | 21/6.9 | TOSHIBA | 2015 | 8.4 | 7 | 10979.304 | 70981.764 | 89.04 | 766.416 | 9 | 8 | 6 | 4 | 0.6666666667 | 1.285714286 | 0.75 | Partial discharge,Low Temprature thermal fault, | Arching | Partial discharge, Normal | 0.6666666667 | 1.285714286 | 0.75 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.285714286 | 0.6666666667 | 0.4444444444 | 2 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
452 | 6007247 | 285 MVA | 21/420/√3 KV | BHEL | 2016 | 8 | 8 | 8707.36 | 69505.12 | 64.8 | 564.48 | 7 | 8 | 9 | 7 | 0.7777777778 | 0.875 | 1.125 | Partial discharge,Low Temprature thermal fault, | Arching | Low Temprature thermal Fault,Thermal Fault<700c | 0.7777777778 | 0.875 | 1.125 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.875 | 0.7777777778 | 1 | 1.142857143 | Arching | Arching | Arching | Thermal Decomposition,corona
453 | 6007246 | 285 MVA | 21/420/√3 KV | BHEL | 2016 | 8.4 | 8 | 11771.172 | 70786.632 | 82.068 | 762.468 | 6 | 5 | 9 | 2 | 0.2222222222 | 0.75 | 1.8 | Partial discharge,Low Temprature thermal fault, | Arching | Low Temprature thermal Fault,Thermal Fault<700c | 0.2222222222 | 0.75 | 1.8 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.75 | 0.2222222222 | 0.3333333333 | 2.5 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
454 | 6007245 | 285 MVA | 21/420/√3 KV | BHEL | 2016 | 8.2 | 5 | 10634.416 | 70119.266 | 73.964 | 657.804 | 5 | 9 | 8 | 9 | 1.125 | 1 | 0.8888888889 | Arching | Arching | Partial discharge, Normal | 1.125 | 1 | 0.8888888889 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 1 | 1.125 | 1.8 | 1 | Arching | Arching | Arching | Thermal Decomposition,corona
455 | 90118A/03 | 70 MVA | 22/6.9/12 | VIJAY ELECTRICAL | 2013 | 7 | 4 | 9775.5 | 58707.18 | 85.75 | 608.51 | 9 | 9 | 7 | 2 | 0.2857142857 | 2.25 | 0.7777777778 | Partial discharge,Low Temprature thermal fault, | Arching | Partial discharge, Normal | 0.2857142857 | 2.25 | 0.7777777778 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 2.25 | 0.2857142857 | 0.2222222222 | 4.5 | Thermal Decomposition, | Thermal Decomposition, | Thermal Decomposition,corona | Thermal Decomposition,corona
456 | 90118A/04 | 70 MVA | 220/6.9/12 | VIJAY ELECTRICAL | 2013 | 7.5 | 3 | 10032 | 63578.4 | 78.45 | 682.425 | 7 | 6 | 5 | 9 | 1.8 | 2.333333333 | 0.8333333333 | Arching | Arching | Partial discharge, Normal | 1.8 | 2.333333333 | 0.8333333333 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 2.333333333 | 1.8 | 1.285714286 | 0.6666666667 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
457 | BH-8791/4 | 40 MVA | 230/11 KV | CGL | 2001 | 7.1 | 6 | 10851.64 | 56995.463 | 197.664 | 2104.369 | 10.153 | 4 | 8 | 8 | 1 | 1.692166667 | 2 | Arching | Arching | Low Temprature thermal Fault,Thermal Fault<700c | 1 | 1.692166667 | 2 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.692166667 | 1 | 0.7879444499 | 0.5 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
458 | BH-8791/5 | 40 MVA | 230/11 KV | ALSTOM | 2001 | 7.5 | 9 | 13259.55 | 58978.35 | 169.8 | 1847.325 | 13.35 | 9.075 | 9 | 7 | 0.7777777778 | 1.483333333 | 0.9917355372 | Partial discharge,Low Temprature thermal fault, | Arching | Partial discharge, Normal | 0.7777777778 | 1.483333333 | 0.9917355372 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.483333333 | 0.7777777778 | 0.5243445693 | 1.296428571 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
459 | BH-8791/3 | 40 MVA | 230/11 KV | ALSTOM | 2001 | 7.8 | 9.984 | 14292.252 | 60179.262 | 217.152 | 2229.552 | 9.672 | 6.708 | 25.35 | 5 | 0.1972386588 | 0.96875 | 3.779069767 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Arching,Thermal Fault > 700 c | 0.1972386588 | 0.96875 | 3.779069767 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.96875 | 0.1972386588 | 0.5169561621 | 1.3416 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
460 | 092Y0003/1 | 40 MVA | 220/11 KV | KIRLOSKAR | 2009 | 8.4 | 8.148 | 12418.56 | 68083.764 | 262.584 | 2691.738 | 13.776 | 9 | 6 | 9 | 1.5 | 1.690721649 | 0.6666666667 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 1.5 | 1.690721649 | 0.6666666667 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.690721649 | 1.5 | 0.6533101045 | 1 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
461 | D-29758 | 40 MVA | 220/11 KV | ALSTOM | 2003 | 7.6 | 12.084 | 15540.48 | 57198.132 | 190.836 | 2236.528 | 7.904 | 7 | 8 | 5 | 0.625 | 0.6540880503 | 1.142857143 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.625 | 0.6540880503 | 1.142857143 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.6540880503 | 0.625 | 0.6325910931 | 1.4 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
462 | 2016629 | 40 MVA | 230/11 KV | BHEL | 2004 | 7 | 6.02 | 11921.56 | 54676.51 | 219.73 | 2304.05 | 6.58 | 6 | 4.55 | 8 | 1.758241758 | 1.093023256 | 0.7583333333 | Arching | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 1.758241758 | 1.093023256 | 0.7583333333 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.093023256 | 1.758241758 | 1.215805471 | 0.75 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
463 | - | 15 MVA | 33/11.5 KV | TOSHIBA | - | 8.2 | 8.856 | 15371.556 | 63749.096 | 164.492 | 1681.328 | 15.744 | 4 | 9 | 4 | 0.4444444444 | 1.777777778 | 2.25 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 0.4444444444 | 1.777777778 | 2.25 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.777777778 | 0.4444444444 | 0.2540650407 | 1 | Thermal Decomposition, | Thermal Decomposition, | Thermal Decomposition,corona | Thermal Decomposition,corona
464 | - | 15 MVA | 33/11.5 KV | TOSHIBA | - | 8.6 | 19.264 | 17423.772 | 65489.602 | 160.218 | 1731.438 | 15.05 | 8 | 15.566 | 7 | 0.4496980599 | 0.78125 | 1.94575 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.4496980599 | 0.78125 | 1.94575 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.78125 | 0.4496980599 | 0.4651162791 | 1.142857143 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
465 | - | 15 MVA | 33/11.5 KV | TOSHIBA |  | 7.6 | 13.072 | 14817.872 | 57328.244 | 226.328 | 2904.264 | 14.744 | 8 | 9 | 3 | 0.3333333333 | 1.127906977 | 1.125 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 0.3333333333 | 1.127906977 | 1.125 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.127906977 | 0.3333333333 | 0.203472599 | 2.666666667 | Thermal Decomposition, | Thermal Decomposition, | Thermal Decomposition,corona | Thermal Decomposition,corona
466 | 8791/1 | 40 MVA | 230/11 KV | CGL | 2011 | 7.2 | 10.224 | 12821.4 | 56648.808 | 194.976 | 1673.208 | 6.768 | 9 | 6 | 9 | 1.5 | 0.661971831 | 0.6666666667 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1.5 | 0.661971831 | 0.6666666667 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.661971831 | 1.5 | 1.329787234 | 1 | Arching | Arching | Arching | Thermal Decomposition,corona
467 | 2016864 | 25 MVA | 33/6.9 KV | BHEL | 2004 | 7.6 | 8.968 | 15270.908 | 58720.564 | 130.264 | 1380.54 | 7.448 | 7 | 9 | 3 | 0.3333333333 | 0.8305084746 | 1.285714286 | Partial discharge,Low Temprature thermal fault, | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 0.3333333333 | 0.8305084746 | 1.285714286 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.8305084746 | 0.3333333333 | 0.402792696 | 2.333333333 | Arching | Thermal Decomposition, | Arching | Thermal Decomposition,corona
468 | 2017091 | 25 MVA | 33/6.9 KV | BHEL | 2005 | 8.2 | 11.48 | 14451.762 | 64077.178 | 219.924 | 2380.05 | 6.314 | 8 | 6 | 9 | 1.5 | 0.55 | 0.75 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1.5 | 0.55 | 0.75 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.55 | 1.5 | 1.425403864 | 0.8888888889 | Arching | Arching | Arching | Thermal Decomposition,corona
469 | 2016865 | 25 MVA | 33/6.9 KV | BHEL | 2004 | 7.8 | 23.478 | 14240.772 | 60883.368 | 171.288 | 1859.52 | 7.956 | 6 | 4 | 4 | 1 | 0.3388704319 | 0.6666666667 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1 | 0.3388704319 | 0.6666666667 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.3388704319 | 1 | 0.5027652086 | 1.5 | Arching | Arching | Arching | Thermal Decomposition,corona
470 | 0824014/1 | 25 MVA | 33/6.9 KV | KIRLOSKAR | 2006 | 7.4 | 14.948 | 11728.482 | 58559.9 | 208.162 | 2961.036 | 12.358 | 10.656 | 9 | 9 | 1 | 0.8267326733 | 0.8445945946 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1 | 0.8267326733 | 0.8445945946 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.8267326733 | 1 | 0.7282731834 | 1.184 | Arching | Arching | Arching | Thermal Decomposition,corona
471 | 05ZG-007/01 | 25 MVA | 33/6.9 KV | KIRLOSKAR | - | 7 | 16.17 | 13626.83 | 51423.33 | 132.3 | 1333.36 | 565.25 | 736.96 | 1448.02 | 9 | 0.006215383765 | 34.95670996 | 1.964855623 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 0.006215383765 | 34.95670996 | 1.964855623 | Thermal Fault> 300c and<700 c | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 34.95670996 | 0.006215383765 | 0.01592215834 | 81.88444444 | Thermal Decomposition, | Thermal Decomposition, | Thermal Decomposition,corona | Thermal Decomposition,corona
472 | 05ZG-007/02 | 25 MVA | 33/6.9 KV | KIRLOSKAR | - | 7.9 | 11.06 | 13759.904 | 62205.153 | 162.424 | 1671.877 | 8.69 | 7.663 | 9 | 9 | 1 | 0.7857142857 | 1.174474749 | Arching | Arching,Low temprature thermal fault | Low Temprature thermal Fault,Thermal Fault<700c | 1 | 0.7857142857 | 1.174474749 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.7857142857 | 1 | 1.035673188 | 0.8514444444 | Arching | Arching | Arching | Thermal Decomposition,corona
473 | 2015969 | 40 MVA | 230/11 KV | BHEL | 2003-04 | 7.6 | 8.36 | 14002.62 | 59336.848 | 204.212 | 1917.48 | 10.944 | 5.472 | 8 | 6 | 0.75 | 1.309090909 | 1.461988304 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 0.75 | 1.309090909 | 1.461988304 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.309090909 | 0.75 | 0.548245614 | 0.912 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
474 | 2015970 | 40 MVA | 230/11 KV | BHEL | 2003-04 | 8 | 96.08 | 12754.24 | 64650.24 | 132.16 | 1368.32 | 53.44 | 2.56 | 8 | 8 | 1 | 0.556203164 | 3.125 | Arching | Arching,Low temprature thermal fault | Arching,Thermal Fault > 700 c | 1 | 0.556203164 | 3.125 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.556203164 | 1 | 0.1497005988 | 0.32 | Arching | Arching | Thermal Decomposition,corona | Arching
475 | D-8305 | 11 MVA | 33/2.64 KV | AREVA | 2009 | 7.1 | 10.792 | 12854.408 | 55862.871 | 159.537 | 1703.006 | 9.514 | 9 | 6 | 9 | 1.5 | 0.8815789474 | 0.6666666667 | Arching | Arching,Low temprature thermal fault | Partial discharge, Normal | 1.5 | 0.8815789474 | 0.6666666667 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.8815789474 | 1.5 | 0.9459743536 | 1 | Arching | Arching | Arching | Thermal Decomposition,corona
476 | 223381880/110 | 16 MVA | 132/6.9 KV | SCHNEIDER | 2021 | 7.3 | 2 | 8816.283 | 62788.395 | 58.327 | 381.279 | 7 | 6 | 8 | 8 | 1 | 3.5 | 1.333333333 | Arching | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 1 | 3.5 | 1.333333333 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 3.5 | 1 | 1.142857143 | 0.75 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
477 | 66190 | 28 MVA | 33/0.310 KV | Tamini | 2010 | 7.4 | 3 | 12914.702 | 59201.85 | 105.968 | 1207.754 | 6 | 7 | 9 | 9 | 1 | 2 | 1.285714286 | Arching | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 1 | 2 | 1.285714286 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 2 | 1 | 1.5 | 0.7777777778 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
478 | 66189 | 28 MVA | 33/0.310 KV | Tamini | 2010 | 8.1 | 4.536 | 13652.145 | 64820.574 | 141.102 | 1581.201 | 7.695 | 9 | 9 | 22.386 | 2.487333333 | 1.696428571 | 1 | Arching | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 2.487333333 | 1.696428571 | 1 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.696428571 | 2.487333333 | 2.909161793 | 0.4020369874 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
479 | T09548/4 | 80 MVA | 141.2/35.3 KV | CGL | 2010 | 7.2 | 9 | 12559.32 | 56803.32 | 139.824 | 1514.376 | 59.616 | 27.936 | 52.128 | 27.473 | 0.5270296194 | 6.624 | 1.865979381 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 0.5270296194 | 6.624 | 1.865979381 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 6.624 | 0.5270296194 | 0.4608326624 | 1.01685291 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
480 | 12067-004 | 80 MVA | 141.2/35.3 KV | ABB | 2010 | 7.5 | 0.9 | 14275.875 | 58915.05 | 92.175 | 891.675 | 8 | 9 | 9 | 4 | 0.4444444444 | 8.888888889 | 1 | Partial discharge,Low Temprature thermal fault, | Low temperature thermal | Low Temprature thermal Fault,Thermal Fault<700c | 0.4444444444 | 8.888888889 | 1 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 8.888888889 | 0.4444444444 | 0.5 | 2.25 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
481 | 90118-B-06 | 50 MVA | 21/6.9 KV | TOSHIBA | 2015 | 2.9 | 6 | 2909.831 | 25198.216 | 53.302 | 598.444 | 7 | 8 | 6 | 3 | 0.5 | 1.166666667 | 0.75 | Partial discharge,Low Temprature thermal fault, | Arching | Partial discharge, Normal | 0.5 | 1.166666667 | 0.75 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.166666667 | 0.5 | 0.4285714286 | 2.666666667 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
482 | 90118-B-03 | 50 MVA | 21/6.9 KV | TOSHIBA | 2015 | 3 | 8 | 4384.95 | 24794.16 | 45.12 | 508.23 | 9 | 7 | 5 | 7 | 1.4 | 1.125 | 0.7142857143 | Arching | Arching | Partial discharge, Normal | 1.4 | 1.125 | 0.7142857143 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.125 | 1.4 | 0.7777777778 | 1 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
483 | T-8241/1 | 14MVA | 11/6.9KV | Crompton Greaves | 1990 | 6.8 | 6.732 | 11497.916 | 54701.376 | 114.172 | 1278.196 | 7 | 5 | 8 | 9 | 1.125 | 1.039809863 | 1.6 | Arching | Low temperature thermal | Low Temprature thermal Fault,Thermal Fault<700c | 1.125 | 1.039809863 | 1.6 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.039809863 | 1.125 | 1.285714286 | 0.5555555556 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
484 | JN-22856 | 10 MVA | 11/6.9KV | VOLTAMP | 2018 | 7.8 | 2 | 14117.766 | 61654.71 | 122.85 | 1333.644 | 8 | 9 | 9 | 8 | 0.8888888889 | 4 | 1 | Partial discharge,Low Temprature thermal fault, | Low temperature thermal | Low Temprature thermal Fault,Thermal Fault<700c | 0.8888888889 | 4 | 1 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 4 | 0.8888888889 | 1 | 1.125 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
485 | 680700644-D7588 | 10 MVA | 11/6.9KV | AREVA | 2008 | 8.1 | 7 | 13725.936 | 65259.27 | 136.7766 | 1450.548 | 6 | 6 | 7 | 8 | 1.142857143 | 0.8571428571 | 1.166666667 | Arching | Arching | Low Temprature thermal Fault,Thermal Fault<700c | 1.142857143 | 0.8571428571 | 1.166666667 | Discharge of Low Energy, | High Energy Discharge | Thermal Fault >700 c | 0.8571428571 | 1.142857143 | 1.333333333 | 0.75 | Arching | Arching | Arching | Thermal Decomposition,corona
486 | T-8241/2 | 14MVA | 11/6.9KV | Crompton Greaves | 1990 | 7.4 | 5 | 11665.36 | 59947.178 | 134.088 | 1486.216 | 9 | 9 | 6 | 6 | 1 | 1.8 | 0.6666666667 | Arching | Arching | Partial discharge, Normal | 1 | 1.8 | 0.6666666667 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.8 | 1 | 0.6666666667 | 1.5 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
487 | 14637/2 | 10 MVA | 11/0.433 KV | VOLTAMP | 2009 | 7 | 8 | 10616.48 | 56746.69 | 137.13 | 1452.15 | 9 | 7 | 9 | 4 | 0.4444444444 | 1.125 | 1.285714286 | Partial discharge,Low Temprature thermal fault, | Arching | Low Temprature thermal Fault,Thermal Fault<700c | 0.4444444444 | 1.125 | 1.285714286 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.125 | 0.4444444444 | 0.4444444444 | 1.75 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
488 | 14637/1 | 10 MVA | 11/0.433 KV | VOLTAMP | 2009 | 7.5 | 6 | 11096.25 | 61612.125 | 148.875 | 1510.8 | 1.5 | 5 | 9 | 45 | 5 | 0.25 | 1.8 | Arching | Arching | Low Temprature thermal Fault,Thermal Fault<700c | 5 | 0.25 | 1.8 | Discharge of Low Energy, | Discharge of Low Energy | Thermal Fault >700 c | 0.25 | 5 | 30 | 0.1111111111 | Arching | Arching | Arching | Arching
489 | JN-8232/3 | 25 MVA | 66/11 KV | VOLTAMP | 2004 | 6.5 | 52.52 | 9492.925 | 52218.66 | 211.64 | 2342.925 | 51.935 | 4.03 | 110.63 | 115 | 1.03950104 | 0.9888613861 | 27.4516129 | Arching | Arching,Low temprature thermal fault | Arching,Thermal Fault > 700 c | 1.03950104 | 0.9888613861 | 27.4516129 | High Energy Discharges | High Energy Discharge | Thermal Fault >700 c | 0.9888613861 | 1.03950104 | 2.214306344 | 0.03504347826 | Arching | Arching | Arching | Arching
490 | JN-8232/3 | 25 MVA | 66/11 KV | VOLTAMP | 2004 | 100 | 11 | 73424 | 915402 | 154 | 1477 | 16 | 12 | 9 | 8 | 0.8888888889 | 1.454545455 | 0.75 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Partial discharge, Normal | 0.8888888889 | 1.454545455 | 0.75 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.454545455 | 0.8888888889 | 0.5 | 1.5 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
491 | 20104037TIG013-002 | 270 MVA | 765/22 KV | Hyundai | 2012 | 7.3 | 4.964 | 11931.266 | 58848.074 | 112.785 | 1215.085 | 6 | 6 | 6 | 7 | 1.166666667 | 1.208702659 | 1 | Arching | Low temperature thermal | Low Temprature thermal Fault,Thermal Fault<700c | 1.166666667 | 1.208702659 | 1 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.208702659 | 1.166666667 | 1.166666667 | 0.8571428571 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
492 | 20150686TIG003 | 270 MVA | 765/22 KV | Hyundai | 2016 | 7.4 | 8 | 12781.65 | 59376.934 | 83.99 | 904.428 | 8 | 5 | 5 | 9 | 1.8 | 1 | 1 | Arching | Arching | Low Temprature thermal Fault,Thermal Fault<700c | 1.8 | 1 | 1 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 1 | 1.8 | 1.125 | 0.5555555556 | Arching | Arching | Arching | Thermal Decomposition,corona
493 | B-30654 | 275 MVA | 420/13/21 KV | ALSTOM | 2013 | 7.1 | 4 | 9421.487 | 60284.254 | 64.184 | 641.769 | 9 | 8 | 9 | 6 | 0.6666666667 | 2.25 | 1.125 | Partial discharge,Low Temprature thermal fault, | Arching | Low Temprature thermal Fault,Thermal Fault<700c | 0.6666666667 | 2.25 | 1.125 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 2.25 | 0.6666666667 | 0.6666666667 | 1.333333333 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
494 | B-30655 | 275 MVA | 420/3/21 KV | ALSTOM | 2013 | 6.4 | 4 | 9660.48 | 53137.152 | 75.904 | 771.456 | 9 | 5 | 7 | 8 | 1.142857143 | 2.25 | 1.4 | Arching | Arching | Low Temprature thermal Fault,Thermal Fault<700c | 1.142857143 | 2.25 | 1.4 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 2.25 | 1.142857143 | 0.8888888889 | 0.625 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
495 | B-30656 | 275 MVA | 420√3/21 KV | ALSTOM | 2013 | 7.3 | 2 | 10475.281 | 60785.932 | 68.839 | 728.029 | 2.263 | 8 | 5 | 6 | 1.2 | 1.1315 | 0.625 | Arching | Arching | Partial discharge, Normal | 1.2 | 1.1315 | 0.625 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.1315 | 1.2 | 2.651347768 | 1.333333333 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
496 | B-30651 | 275 MVA | 420√3/21 KV | ALSTOM | 2012 | 7 | 1 | 10622.43 | 57277.08 | 111.02 | 1050.42 | 2.87 | 9 | 8 | 9 | 1.125 | 2.87 | 0.8888888889 | Arching | Arching | Partial discharge, Normal | 1.125 | 2.87 | 0.8888888889 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 2.87 | 1.125 | 3.135888502 | 1 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
497 | B-30657 | 275 MVA | 420√3/21 KV | ALSTOM | 2013 | 6.7 | 4.489 | 11388.526 | 54404.134 | 56.615 | 603.536 | 6.097 | 5 | 8.576 | 6 | 0.6996268657 | 1.358208955 | 1.7152 | Partial discharge,Low Temprature thermal fault, | Thermal Fault <700c, thermal fault >700c | Low Temprature thermal Fault,Thermal Fault<700c | 0.6996268657 | 1.358208955 | 1.7152 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.358208955 | 0.6996268657 | 0.9840905363 | 0.8333333333 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona
498 | B-30653 | 275 MVA | 420√3/21 KV | ALSTOM | 2012 | 6.5 | 1.3 | 7909.395 | 55733.015 | 70.98 | 798.33 | 4 | 8 | 9 | 9 | 1 | 3.076923077 | 1.125 | Arching | Low temperature thermal | Low Temprature thermal Fault,Thermal Fault<700c | 1 | 3.076923077 | 1.125 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 3.076923077 | 1 | 2.25 | 0.8888888889 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
499 | C-10243 | 40 MVA | 21/11.5 KV | ALSTOM | 2013 | 6.4 | 8 | 11809.344 | 50937.92 | 97.408 | 830.592 | 6 | 8 | 8 | 9 | 1.125 | 0.75 | 1 | Arching | Arching | Low Temprature thermal Fault,Thermal Fault<700c | 1.125 | 0.75 | 1 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.75 | 1.125 | 1.5 | 0.8888888889 | Arching | Arching | Arching | Thermal Decomposition,corona
500 | C-10242 | 40 MVA | 21/11.5 KV | ALSTOM | 2012 | 7.9 | 9 | 13239.057 | 63853.33 | 112.97 | 1032.688 | 8 | 9 | 7 | 8 | 1.142857143 | 0.8888888889 | 0.7777777778 | Arching | Arching | Partial discharge, Normal | 1.142857143 | 0.8888888889 | 0.7777777778 | Discharge of Low Energy, | High Energy Discharge | thermal fault <300c | 0.8888888889 | 1.142857143 | 1 | 1.125 | Arching | Arching | Arching | Thermal Decomposition,corona
501 | C-10181 | 10 MVA | 11/3.45 KV | ALSTOM | 2012 | 6.8 | 2 | 9796.42 | 55987.664 | 117.368 | 1183.948 | 9 | 8 | 6 | 7 | 1.166666667 | 4.5 | 0.75 | Arching | Low temperature thermal | Partial discharge, Normal | 1.166666667 | 4.5 | 0.75 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 4.5 | 1.166666667 | 0.7777777778 | 1.142857143 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
502 | C-10180 | 10 MVA | 11/3.45 KV | ALSTOM | 2012 | 7.4 | 3 | 12503.928 | 59133.4 | 135.05 | 1437.82 | 1.554 | 7 | 6 | 6 | 1 | 0.518 | 0.8571428571 | Arching | Arching | Partial discharge, Normal | 1 | 0.518 | 0.8571428571 | High Energy Discharge | High Energy Discharge | thermal fault <300c | 0.518 | 1 | 3.861003861 | 1.166666667 | Arching | Arching | Arching | Thermal Decomposition,corona
503 | C-10241 | 40 MVA | 21/11.5 KV | ALSTOM | 2012 | 6.5 | 5 | 11803.74 | 51513.605 | 89.505 | 1088.815 | 11 | 6 | 5 | 7 | 1.4 | 2.2 | 0.8333333333 | Arching | Arching | Partial discharge, Normal | 1.4 | 2.2 | 0.8333333333 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 2.2 | 1.4 | 0.6363636364 | 0.8571428571 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
504 | C-10244 | 40 MVA | 21/11.5 KV | ALSTOM | 2013 | 6.9 | 8 | 11343.738 | 56442.483 | 81.144 | 713.736 | 12 | 7 | 8 | 8 | 1 | 1.5 | 1.142857143 | Arching | Arching | Low Temprature thermal Fault,Thermal Fault<700c | 1 | 1.5 | 1.142857143 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 1.5 | 1 | 0.6666666667 | 0.875 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
505 | D-11438 | 15 MVA | 33/11 KV | SCHINDER | 2012 | 7.1 | 1.491 | 10290.456 | 59031.388 | 111.967 | 1034.186 | 14 | 8 | 9 | 9 | 1 | 9.389671362 | 1.125 | Arching | Low temperature thermal | Low Temprature thermal Fault,Thermal Fault<700c | 1 | 9.389671362 | 1.125 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | Thermal Fault >700 c | 9.389671362 | 1 | 0.6428571429 | 0.8888888889 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
506 | PC-0400539 | 10 MVA | 33/11 KV | T & R | 2015 | 7 | 5.46 | 12296.9 | 55513.78 | 128.94 | 1503.53 | 6 | 9 | 6 | 8 | 1.333333333 | 1.098901099 | 0.6666666667 | Arching | Low temperature thermal | Partial discharge, Normal | 1.333333333 | 1.098901099 | 0.6666666667 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.098901099 | 1.333333333 | 1.333333333 | 1.125 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
507 | PC-0400539 | 10 MVA | 33/11 KV | T & R | 2015 | 6.9 | 4 | 10847.076 | 56488.437 | 74.52 | 815.235 | 9 | 8 | 8 | 29.67 | 3.70875 | 2.25 | 1 | Arching | Arching | Low Temprature thermal Fault,Thermal Fault<700c | 3.70875 | 2.25 | 1 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 2.25 | 3.70875 | 3.296666667 | 0.2696326255 | Thermal Decomposition, | Arching | Arching | Arching
508 | 82159 | 10 MVA | 33/11 KV | MARSONS | 2013 | 7.8 | 3 | 14528.124 | 61573.512 | 117.78 | 1011.816 | 6 | 29.67 | 9 | 8 | 0.8888888889 | 2 | 0.3033367037 | Partial discharge,Low Temprature thermal fault, | Arching | Partial discharge, Normal | 0.8888888889 | 2 | 0.3033367037 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 2 | 0.8888888889 | 1.333333333 | 3.70875 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
509 | 82159 | 10 MVA | 33/11 KV | MARSONS | 2013 | 7.2 | 5 | 12818.376 | 57338.352 | 84.312 | 939.024 | 8 | 8 | 5 | 6.552 | 1.3104 | 1.6 | 0.625 | Arching | Arching | Partial discharge, Normal | 1.3104 | 1.6 | 0.625 | Discharge of Low Energy, | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.6 | 1.3104 | 0.819 | 1.221001221 | Thermal Decomposition, | Arching | Arching | Thermal Decomposition,corona
510 | PC-0400540 | 10 MVA | 33/11 KV | R & T | 2015 | 6.7 | 7 | 9485.324 | 56073.439 | 85.559 | 949.323 | 4 | 6.552 | 9 | 9 | 1 | 0.5714285714 | 1.373626374 | Arching | Arching | Low Temprature thermal Fault,Thermal Fault<700c | 1 | 0.5714285714 | 1.373626374 | High Energy Discharge | High Energy Discharge | Thermal Fault >700 c | 0.5714285714 | 1 | 2.25 | 0.728 | Arching | Arching | Arching | Thermal Decomposition,corona
511 | PC-0400540 | 10 MVA | 33/11 KV | R & T | 2015 | 7 | 8 | 12377.19 | 55944.56 | 63.56 | 618.59 | 9 | 8 | 8 | 5.67 | 0.70875 | 1.125 | 1 | Arching | Arching | Low Temprature thermal Fault,Thermal Fault<700c | 0.70875 | 1.125 | 1 | High Energy Discharge | Thermal Fault >300c and<700 and >700 c | thermal fault <300c | 1.125 | 0.70875 | 0.63 | 1.410934744 | Thermal Decomposition, | Thermal Decomposition, | Arching | Thermal Decomposition,corona

## Sheet1
DESCRIPTION OF DGA DATA |  |  | DESCRIPTION OF DGA DATA |  |  | DESCRIPTION OF DGA DATA
Rogers Ratio Method |  |  | IEC Ratio Method |  |  | Dornenburg Ratio Method
FAULT TYPE | FAULT CODE | NUMBER OF SAMPLES | FAULT TYPE | FAULT CODE | NUMBER OF SAMPLES | FAULT TYPE | FAULT CODE | NUMBER OF SAMPLES
|  | DATASET 1 |  |  | DATASET 1 |  |  | DATASET 1
Arching |  | 607 | Partial discharges |  | 14 | Thermal Decomposition |  | 853
Partial discharge |  | 461 | Discharges of low energy |  | 243 | Corona |  | 459
Low temperature thermal fault |  | 632 | High energy discharges |  | 497 | Arching |  | 1179
Thermal fault <700°C |  | 177 | Thermal faults<300°C |  | 0
Thermal fault >700°C |  | 177 | Thermal faults>300°C and <700°C |  | 8
|  |  | Thermal faults>700°C |  | 479
Total |  | 2054 | Total |  | 1241 | Total |  | 2491